BLACK LIQUOR RECOVERY BOILER

ADVISORY COMMITTEE

### MINUTES OF MEETING

### April 9, 2025

OBJECTIVE

BLRBAC’s objective is to promote improved safety of chemical recovery boilers and their auxiliaries through the interchange of technical knowledge, experience, and data on past and any future recovery boiler incidents.	Bylaws - 2.1

OFFICERS

Chairman:     Gregory Burns

Mt Pleasant, SC			                Cell: 843-991-7192

Domtar                                                              gregory.burns@domtar.com

Vice-Chair:    David Tjaarda

Smurfit Westrock                                                         Cell: 503-728-2550

Charleston, TN                                                           dave.tjaarda@smurfitwestrock.com

Secretary:      Daniel Franco

Recovery Specialist                                                Cell: +573113001079

Cali, Colombia                                                        danielf721@gmail.com

Treasurer:      Brad Osbourne

Electron Machine                                                Cell: 352-267-0118

Umatilla, FL                                                      brad@electronmachine.com

REGULAR MEMBERSHIP

Organizations operating, manufacturing, or insuring chemical recovery boilers are eligible.

ASSOCIATE MEMBERSHIP

Organizations having a direct interest or role in the safety of chemical recovery boilers are eligible.

CORRESPONDING MEMBERSHIP

Companies residing outside of the United States which finds it impractical to attend meetings on a regular basis because of distance and expenses, but desires to be involved and informed of BLRBAC activities.

Bylaws - 3.1

BLRBAC INTERNET ADDRESS: ---- www.blrbac.net

IRS Employer ID/Tax ID (IRS E.I.N.T./T.I.N.) ----

EXUTIVE COMMITTEE

Gregory Burns                                                                                     Jimmy Onstead

BLRBAC Chairman                                                                              Insurance Representative

Domtar                                                                                                 FM Global

Mt Pleasant, SC                                                                                   Frisco, TX

Cell: 843-991-7192                                                                      Tel:  972-731-1656

gregory.burns@domtar.com                                                      Cell: 903-744-2734

jimmy.onstead@fmglobal.com

David Tjaarda                                                                                    Evangelos Townsend (Ev)

BLRBAC Vice Chairman                                                                   Manufacturing Representative

Smurfit Westrock                                                                              Babcock & Wilcox

Charleston, TN                                                                                  Melissa, TX

Cell: 503-728-2550                                                                           Office: (281) 405-6825

dave.tjaarda@smurfitwestrock.com                                              Mobile: (469) 815-8395

emtownsend@babcock.com

Daniel Franco                                                                                   Scott Moyer

BLRBAC Secretary                                                                           Operator Representative

Recovery Specialist                                                                 Smurfit Westrock

Cali, Colombia                                                                        Jacksonville, FL

Cell: +573113001079                                                             Mobile: 904.437.7149

danielf721@gmail.com                                                      scott.moyer@smurfitwestrock.com

Brad Osborne

BLRBAC Treasurer

Electron Machine

Umatilla, FL

Cell: 352-267-0118

brad@electronmachine.com

BLRBAC SUBCOMMITTEES

| AUXILIARY FUEL Tom DeBeer – Chairman LCK Consultants 5001 Willow Creek Drive Woodstock, GA 30188 Cell:(404) 218-8613 tdebeer2024@gmail.com | ##### BLACK LIQUOR, SAFE FIRING OF ##### Vernon Blackard, Chairman International Paper Roy, MT 59471 Cell: 251-284-3471 vernon.blackard@ipaper.com |
| --- | --- |
| EMERGENCY SHUTDOWN PROCEDURES Frank Navojosky, Chairman BSI Loveland, OH Cell: (513) 334-9999 fcnavojo@gmail.com | FIRE PROTECTION IN DIRECT CONTACT EVAPORATORS Stephen Cox - Chairman International Paper Maumelle, AR Tel: 409-779-7104 stephen.cox@ipaper.com |
| INSTRUMENTATION John Browning, Chairman Georgia Pacific Atlanta, GA Tel: 251-593-6096 john.browning@GAPAC.com | MATERIALS & WELDING Laura Nicol–Chairperson ‡ Babcock & Wilcox 1200 E Market St, Ste 650 Akron, OH 44305 Cell: 330-361-0217 lsnicol@babcock.com |
| PERSONNEL SAFETY Ward Benjiman - Chairman Sappi North America Skowhegan, ME Tel: 207-238-7686 Benjiman.Ward@sappi.com | PUBLICITY & NEWS RELEASE Matt Paine, Chairman FM Norwood, MA Tel: 781-255-4733 matthew.paine@fmglobal.com |
| WASTE STREAMS Paul Seefeld, Chairman A.H. Lundberg Associates, Inc. Jacksonville, FL Tel: 904-614-6492 paul.seefeld@lundberg-us.com | WATER TREATMENT Tom Przybylski, Chairman Power Specialists Associates Somers, CT ### Tel: 860-763-3241 tom.@psaengineering.com |

FUTURE BLRBAC MEETINGS

| Fall | October | 6,7,8 | 2025 |
| --- | --- | --- | --- |
| Spring | April | 6,7,8 | 2026 |

"Bring Operator(s).  Give them a chance to hear firsthand!"

Past Chairman Frank Navojosky

###### *****************************

* NOTE:  For varying reasons, the previously published meeting dates have been changed at the

discretion of the Executive Committee.

###### BLRBAC has established its own website at:  www.blrbac.net

At this website you will find a copy of past Meeting Minutes and the next Meeting Notice.  Therefore, each Representative and Associate Representative is asked to inform their people of this WEB site.  This is where they can obtain the following BLRBAC documents:

BLRBAC MEETING NOTICE

COVER LETTER			General Information

REGISTRATION FORM 	Will be available on the website with a link to register and pay on line.

HILTON Airport	Blocked room dates, pricing, address, hotel phone numbers

SCHEDULE				 List of subcommittee activities on Monday and Tuesday

AGENDA	 Reports given to Joint BLRBAC Meeting on Wednesday

OPERATING PROBLEMS	Mail/e-mail completed questionnaires to David Tjaarda

QUESTIONNAIRE	The Vice Chairman and he will see that your concerns are brought up and discussed during the Operating Problems session at the next meeting.

These are available at the BLRBAC INTERNET ADDRESS: www.blrbac.net

BLRBAC Guidelines & Recommended Practices

LEGAL NOTICE

Recommended Good Practice For Design, Operation, and Testing of the Emergency Shutdown System for Black Liquor Recovery Boilers

(Dated: October 2024)

Safe Firing of Black Liquor in Black Liquor Recovery Boilers

(Dated: October 2023)

Materials & Welding Guidelines

(Dated: April 2013)

Safe Firing of Auxiliary Fuel in Black Liquor Recovery Boilers

(Dated: February 2012)

Fire Protection in Direct Contact Evaporators and Associated Equipment

(Dated: February 2024)

Personnel Safety & Training

(Dated: April 2018)

Application of Rotork Actuators on Black Liquor Recovery Boilers

(Dated: April 2025)

Boiler Water Management Guidelines for Black Liquor Recovery Boiler

(Dated: April 2023)

Instrumentation Checklist and Classification Guide for Instruments and Control Systems Used in the Operation of Black 9Liquor Recovery Boilers (Dated: April 2023)

Thermal Oxidation of Waste Streams in Black Liquor Recovery Boilers

(Dated: April 2021)

If you have any questions, contact:

Secretary:	Daniel Franco		Tel:  +576023258865

Recovery Specialist Retired	Cell: +573113001079

Cali, Colombia                                                         danielf721@gmail.com

AUXILIARY FUEL SUBCOMMITTEE

Tom DeBeer – Chairman‡

LCK Consultants

5001 Willow Creek Drive

Woodstock, GA 30188

Cell:(404) 218-8613

tdebeer2024@gmail.com

| David Frazier New Member‡ International Paper | John Lewis‡ General Electric Vernova 200 Great Pond Drive G3W4 Windsor, CT 06095 Tel:(860) 285-2918 john.c.lewis@ge.com | Michael Bekech CECO - CCA Combustion Systems 884 Main St. Monroe, CT 06468 Tel: (203) 268-3139 x 137 Cell: (203) 895-4822 mbekech@onececo.com |
| --- | --- | --- |
| Mike Bruce Sylvamo 104 Putnam Center Road Putnam Station, N.Y. 12861 Tel: (518) 586-6954 mike.bruce@sylvamo.com | Rick Dooks Fossil Power Systems Inc 10 Mosher Drive Dartmouth, Nova Scotia B3B 1N5 Canada Cell: 1-902-499-0546 dooksr@fossil.ca | Chris Finnemore Georgia Pacific Fernandina Beach, FL 32034 Cell: (904) 321-6861 Chris.finnemore@GAPAC.com |
| Travis Flower Babcock & Wilcox Company P. O. Box 351 Barberton, OH 44203-0315 Tel: (330) 860-6042 taflower@babcock.com | Derrick Gossen‡ FM 301 Freedom Ct. Mishicot, WI 54228 Cell: (920) 619-1750 derrick.gossen@fmglobal.com | Brook M. Holland Bodman Services LLC Cell: (828) 421-0487 brookmholland@gmail.com |
| Greg Imig‡ Andritz 5405 Windward Pkwy, Suite 100W Alpharetta, GA 30004 Tel: (770) 640-2633 Cell: (404) 545-9076 greg.imig@andritz.com | Carlos Rojas Smurfit Westrock (Colombia) (TBD) Colombia, S. America Phone: +573113009193 carlos.rojas@smurfitwestrock.co |  |

| ‡ = | Denotes attendance at last meeting, April 9, 2025 |
| --- | --- |
| * = | Denotes a new/replacing member |

EMERGENCY SHUTDOWN PROCEDURES SUBCOMMITTEE

Frank Navojosky– Chairman‡

BSI

Cell: (513) 334-9999

fcnavojo@gmail.com

| Dean Clay, Secretary‡ Boiler Services & Inspection, LLC BSI Cell: (513) 497-9070 dclayesp@gmail.com | Scott Crysel‡ FM One Cowboys Way, Suite 600 Frisco, TX 75034 Tel: (972) 731-1658 Fax: (972) 731-1820 scott.crysel@fmglobal.com | James Franks‡ AXA XL Risk Consulting 855 Dogwood Road Somerville, TN 38068 Tel: (901) 465-0771 Fax: (888) 964-7348 james.franks@axaxl.com |
| --- | --- | --- |
| Mike Bruce‡ Sylvamo 104 Putnam Center Rd Putnam Station, NY Cell: 518-586-6954 mike.bruce@sylvamo.com | Mike Bates WCBLRBAC Chairman Domtar Crofton Office (250) 246-6176 Cell (236) 594-6458 mike.bates@domtar.com | John DeFusco‡ Babcock & Wilcox Company 4 Essex Drive Yarmouth, ME 04096 Cell: (207) 776-0954 jpdefusco@babcock.com |
| Gregory Burns‡ Domtar Cell: (843) 991-7192 Office: 803-802-8077 Fort Mill, SC gregory.burns@domtar.com | Scott Moyer, Vice Chairman‡ Smurfit Westrock 1660 Prudential Drive, Ste. 202 Jacksonville, FL 32207 Cell: 904-437-7149 scott.moyer@smurfitwestrock.com | Greg Zavadoski‡ Georgia Pacific Cell: 715.432.2470 greg.zavadoski@gapac.com |
| John Phillips‡ Andritz Pulp & Paper 5405 Windward Parkway, Suite 100W Alpharetta, GA 30004 Tel: (770) 640-2434 Fax: (770) 640-2521 john.phillips@andritz.com | Dan Cudmore‡ GE Vernova 1420 Blair Towers Place Suite 500 Ottawa, ON K1J 9L8 Tel: (613) 298-5021 dan.cudmore@ge.com | Dave Gadai‡ Valmet Inc 3440 Torington Way Suite 300, Bldg 3 Charlotte, NC 28277 Cell: (704) 560-3575 dave.gadai@valmet.com Jeremiah Yoder, Alternate |

‡ Denotes attendance in Spring 2025 meeting

PUBLICITY & NEWS RELEASE SUBCOMMITTEE

Matt Paine - Chairman

FM

Johnston, RI

Cell: 781-255-4733

matthew.paine@fmglobal.com

FIRE PROTECTION IN DIRECT CONTACT EVAPORATORS

AND ASSOCIATED EQUIPMENT SUBCOMMITTEE

Stephen Cox - Chairman

International Paper

6318 Highway 139

Bastrop, La 71220

Tel: 409-779-7104

Stephen.cox@ipaper.com

| Kevin Huelsbeck - Vice Chair FM Global Property Insurance Forest Products Operations W4893 Cliff View Drive Sherwood, WI 54169 Tel: 920-205-5529 kevin.huelsbeck@fmglobal.com | Robert Orender Georgia Pacific 133 Peachtree Street NE Atlanta, GA 30303 Robert.orender@gapac.com | Robert Goddard XL Group 129 Drive 1143 Tupelo, MS 38804 Tel: 662 844-5897 robert.goddard@axaxl.com |
| --- | --- | --- |
|  |  | Joseph Lynch Swiss Re America Holding Corporation 1150 Sanctuary Parkway, Suite 425 Alpharetta, GA 30009 Tel: 1770-569-8706 Joe_Lynch@swissre.com |
| Mike McKenzie(new for spring 2024) International Paper Bogalusa Mill Tel: 19857328723 Michael.McKenzie1@ipaper.com |  |  |

‡Denotes attendance at the meeting in Fall 2024. Did not meet In Spring 2025

INSTRUMENTATION SUBCOMMITTEE

Spring 2025 members and attendance

‡JC Browning, Jr (1998) – Chairman

Georgia Pacific

133 Peachtree St. NE (30303) Atlanta, GA 30348-5605

Tel: 251-593-6096  john.browning@gapac.com

‡ Attended      New Member       Leaving Member

| C.A. Vossberg (<2000?) ‡ Vice Chairman P Electron Machine Corp. P.O. Box 2349 Umatilla, FL 32784 Tel: 352-406-1351 ca@electronmachine.com | Ben Bunner (2020?) Secretary Andritz 5404 Windward Parkway Suit 100W Alpharetta, GA 30004 Cell: 678-907-7617 ben.bunner@andritz.com | David T. Boudreau (2007) P SAPPI (S.D. Warren Company) 1329 Waterville Road Skowhegan, ME 04976 Tel: 207-314-8024 dave.boudreau@sappi.com |
| --- | --- | --- |
| Joel Byrd (2015?) International Paper Company 12515 Choctaw Rd Bogalusa, La 70427 Tel:985-516-1110 Joel.byrd@ipaper.com | Gordon L. Vandenburg (2000?) Liquid Solids Control, Inc. P.O. Box 259, Farm St. Upton, MA 01568 Tel: (603) 833-8536 gordie@liquidsolidscontrol.com | Jari Sopanen (1995?) Jari Consultoria de Automacao Ltda Rua Rio Grande do Sul, 505 Agua Verde, Curitiba Brazil 80620-080 Tel:+55413244-7059 jari@jariautomation.com |
| Kevin Huelsbeck (2010?) ‡ FM Global P W4893 Cliff View Drive Sherwood, WI 54169 Cell: 920-205-5529 kevin.huelsbeck@fmglobal.com | Ricky Henderson (2024) Vaisala Inc. 3 Van de Graaff Drive. Burlington, MA 01803 (P) 713-550-2534 ricky.henderson@vaisala.com | Andy Clement (2019?) ‡ 10 Mosher Drive P Dartmouth, Nova Scotia Canada B3B 1N5 Tel:902-468-2743 ext.245 clementa@fossil.ca |
| Adam Marickovich (2024) ‡ Georgia-Pacific P 133 Peachtree St. NE (30303) Atlanta, GA 30348-5605d Adam.Marickovich1@gapac.com | Daniel Albert - (2019?) Rotork 675 Mile Crossing Boulevard Rochester NY 14624 (585) 247-2304 Daniel.Albert@Rotorq.com | Daniel Guarnieri (2024) SYLVAMO Rodovia SP 340 KM171 ¦ Mogi Guacu, SP, Brazil 13845-901 T: +55 19 3861-8972 ¦ M: +55 19 97102-1290 daniel.guarnieri@sylvamo.com |
| Patrick Buyck (2024) SAPPI North America P 2201 Avenue B, PO Box 511, Cloquet, MN 55720 Patrick.Buyck@sappi.com | Deshan Naidoo (2024) SAPPI 25 Heron Way Yellowwood Park Durban , South Africa 4004 Deshan.Naidoo@sappi.com | Andrew Kirk (2024) PCA even.saumer@smurfitwestrock.com |
| Chris Clements (2024) Smurfit Westrock Chris.clements@smurfitwestrock.com | Dave Avery P |  |

PERSONNEL SAFETY SUBCOMMITTEE

Ward Benjiman - Chairman‡

Sappi North America

Skowhegan, ME

Tel: 207-238-7686

Benjiman.Ward@sappi.com

| Sam Dean Rayonier Advanced Materials 4470 Savannah Highway Jesup, GA 31545 Tel: (912) 427-5103 samuel.dean@rayonierAM.com | Steve Morrison‡ G-P Cell – (404) 268-6573 Team – (404) 652-7141 Steve.morrison@gapac.com | Tom Edwards B&W twedwards@babcock.com |
| --- | --- | --- |
|  | David Von Oepen Smurfit West Rock 28270 U.S. Highway 80 West Demopolis, AL 36732-5121 Tel: (334) 289-6315 dvonoepen@smurfitwestrock.com | Mathew Glenn‡ Irving Pulp & Paper, Limited Recovery Superintendent P.O. Box 3007 408 Mill Street Saint John, New Brunswick Tel: (506) 634-4234 glenn.matthew@irvingpulp.com |
| Grey Gurkin International Paper International Paper Co. | Zack Payne‡ Andritz 5405 Windward Parkway Suite 100W Alpharetta, GA 30004-3894 Tel: (706) 344-9006 zack.payne@andritz.com | Francisco Britt‡ FM One Cowboys Way Suite 600 Frisco, TX 75034 Tel: (972) 731-2145 Francisco.britt@fmglobal.com |
| Brook Holland‡ G.H. Bodman 228 Wild Rose Lane Canton, NC 28716 Tel : (828) 421-0487 brookmholland@gmail.com | Jake Dowland‡ ND Paper | Sam Miller‡ Andritz |

‡Denotes attendance at the April 2025 meeting

MATERIALS & WELDING SUBCOMMITTEE

Laura Nicols – Chairperson ‡

Babcock & Wilcox

1200 E Market St, Ste 650

Akron, OH 44305

Cell: 330-361-0217

lsnicol@babcock.com

‡ Attendance this meeting

| Materials and Welding Committee Members |  |  |
| --- | --- | --- |
| Jesse Worsham: Vice Chairman ‡ Domtar Paper Tel: (843) 479-0200 Ext 8879 Jesse.Worsham@Domtar.com | *Maxime Simard ‡ FM Cell: (418) 435-1551 maxime.simard @fmglobal.com *Alt: Mark Jackson Mark.Jackson@FMGlobal.com | Scott Lowrie ‡ Andritz, Inc. Scott.Lowrie@andritz.com *Alternate - Mark LeBel ‡ Cell (678) 577-8613 Mark.LeBel@andritz.com |
| Brent Griffin ‡ Georgia-Pacific LLC Cell: (850) 910-1259 brent.griffin@gapac.com *Alt: Chad Harrod ‡ Cell: (404) 395-3064 Chad.Harrod@gapac.com | Jennings Bird Valmet Tel: 803 235 8091 Jennings.bird@valmet.com *Alt: Ron Reed ‡ Tel: (704) 281-3073 Ron.reed@valmet.com | Billy Collett ‡ National Boiler Services, LLC. Cell: (423) 582-6958 bcollett@nationalboiler.com *Alt: Steve Harville Cell: (251) 591-7850 Sharville@NationalBoiler.com |
| Jed Merritt ‡ RMR Mechanical Tel: 601-508-9084 Jed.merritt@rmrmechanical.com *Alt: Ben Rogers Ben.Rogers@rmrmechanical.com | Chris Rawls Applied Technical Services Tel: 757-218-8465 crawls@atslab.com Alt: Thomas Kapperman Tel: (678)231-8025 tkapperman@atslab.com | Stacy Power ‡ Midstate SMS Tel: (843) 957-2111 Cell: (843) 297-1987 spower@smsmidstate.com |
| William Burns ‡ ND Paper – Rumford Cell: 207-743-1029 William.Burns@us.ndpaper.com | TBD Acuren |  |

SAFE FIRING OF BLACK LIQUOR SUBCOMMITTEE

‡Vernon Blackard - Chairman

International Paper

Cell: 251-284-3471

vernon.blackard@ipaper.com

| Clif Barreca International Paper Tel: 252-633-7696 clif.barreca@ipaper.com | ‡Tim Hicks Billerud Tel. 901-468-5058 Tim.hicks@Billerud.com | Joel Byrd International Paper Tel: 85-516-1110 Joel.byrd@ipaper.com |
| --- | --- | --- |
| ‡Sarah Henke – Vice-Chair Valmet Tel: 919-454-3441 Sarah.henke@valmet.com | ‡Peter Donahue Fossil Power Systems, Inc. Tel: 902-468-2743, Ext. 251 Cell: 902-877-9312 donahuep@fossil.ca | Len Erickson Power Specialist Assoc. Tel: 208-841-4246 len.erickson@PSAengineering.com |
| Jason Saulsbury Green Bay Packaging Tel: 902 908 0495 | ‡Wes Hill Georgia Pacific Tel 360-607-4189 Wes.hill@gapac.com | ‡Daniel Franco Recovery Specialist Cell: +57 3113001079 danielf721@gmail.com |
| ‡Guy Labonte FM Global Tel: 514-876-7412 Cell: 514-942-3651 ## guy.labonte@fmglobal.com | ‡Doug Murch Smurfit Westrock Tel: 804-444-5245 Cell: 804-787-0781 douglas.murch@smurfitwestrock.com | ‡Alarick Tavares Smurfit Westrock ### Tel - 678 492-1107 alarick.tavares@smurfitwestrock.com |
| Mark Sargent Bodman Services, LLC Tel: 514-543-0480 ## Mark.sargent@rmrmechanical.com | ‡Pasi Miikkulainen/ Sam Miller substitute ## Andritz p: +1 770 640 2414 m: +1 678 230 1525 Pasi.Miikkulainen@andritz.com | ‡ Brian Rawson International Paper Cell: 850-266-5259 brian.rawson@ipaper.com |
| ‡Jason Lewis ND Paper m: 207-557-0952 ## Jason.lewis@us.ndpaper.com. | Rudy Haraga – Fornax Services Tel: 860-268-1871 ## Rudy.haraga@thefornax.com | ‡Olli Kujanpaa – Georgia Pacific Tel: 404-432-8281 ## Olli.kujanpaa@gapac.com |
| Ryan P Henry Green Bay Packaging Inc. Tel: 501-306-8330 ## rhenry@gbp.com | ## Keijo Pyorala Vaisala keijo.pyorala@vaisala.com | ‡David Tjaarda ### Smurfit Westrock ### Tel – 503 728-2550 dave.tjaarda@smurfitwestrock.com |
| Justin Helton Andritz Tel: 470-416-1342 ## Justin.helton@andritz.com | ‡Evangelos Townsend B&W Office: 281-405-6825 Mobile: 469-815-8395 Emtownsend@babcock.com | ‡Jay Dilworth Pixelle Specialty Solutions Tel 717 225 4711 James.Dilworth@pixelle.com |

‡Denotes attendance at the meeting in Spring of 2025.

WASTE STREAMS SUBCOMMITTEE

### *Paul Seefeld – Chairman

LDX Solutions

9246 Audubon Park Ln S

Jacksonville, FL 32257

Cell: 904-614-6492

### PSeefeld@LDXSolutions.com

| Raquel Posada Smurfit Westrock Columbia ### Raquel.posada@smurfitwestrock.co | ## *Neil Chaudhuri FM Global 100 New Park Place, Suite 200 Vaughan ON Canada L4K OH9 Tel: 647-894-5680 Neil.chaudhuri@fmglobal.com | *David Frazier International Paper Technology 6285 Tri-Ridge Blvd Loveland, Ohio 45140 Cell: 706-305-5321 David.frazier@ipaper.com |
| --- | --- | --- |
| Cobb Golson Westrock Jacksonville, FL Tel: 904-826-7430 Cobb.golson@westrock.com | *John Lewis Fluor 100 Fluor Daniel Drive Greenville, SC 29607-2762 Tel: 864 517-1683 john.lewis@fluorgov.com | Pasi Miikkulainen Andritz 5405 Windward Parkway Alpharetta, GA 30004 Tel:770-640-2414 Cell: 678-230-1525 Pasi.miikkulainen@andritz.com |
| *Oscar Guevara Domtar 100 Kingsley Park Drive Fort Mill, SC 29715 Tel: 479-871-0970 Oscar.guevara@domtar.com |  | Greg Wass LDX Solutions 8271 154th Ave NE Redmond, WA 98052 Office: 425-283-5070 Cell: 425-503-2747 gwass@LDXSolutions.com |
| *Kevin Sapp – Vice Chairman Georgia Pacific Atlanta, GA Tel: 387-227-1038 Kevin.sapp@gapac.com | *Wayne Bucher NORAM Wayne.bucher@gmail.com |  |

*Denotes attendance for the Fall 2024 meeting; Did not meet in the Spring 2025 meeting

WATER TREATMENT SUBCOMMITTEE

Spring 2025

‡Tom Przybylski

Power Specialists Assoc. Inc.

### tom.przybylski@psaengineering.com

| ‡Jeff Armstrong Solenis ### E-mail Address xxx | ‡Rick Baxter Valmet ### E-mail Address richard.baxter@valmet.com | ‡Michael Bayse George H. Bodman, Inc. ### E-mail Address bbayse@aol.com (Substitute: Gene Cotton) |
| --- | --- | --- |
| ‡Fred Call Buckman ### E-mail Address fccall@buckman.com | ‡Frank Crumpler Nalco ### E-mail Address fcrumpler@ecolab.com alternate: Jim Gannon | Susan Childress RMR ### E-mail Address susan.childress@rmrmechanical.com |
| ‡Frank Destefano 3D ### E-mail Address DestefanoFrank55@gmail.com | ‡Don Downey Purolite ### E-mail Address don.downey@purolite.com | Peter Fogg Georgia Pacific ### E-mail Address peter.fogg@gpac.com |
| Nick Wildey Georgia Pacific ### E-mail Address nicholas.wildey@gpac.com | ‡Tom Meehan FM Global ### E-mail Address thomas.meehan@fmglobal.com | ‡Trevor Murray Irving Pulp and Paper ### E-mail Address murray.trevor@irvingpulp.com |
| Dylan Price RMR ### E-mail Address Dyline.price@rmrmechanical.com | ‡Dave Tjaarda Smurfit WestRock ### E-mail Address dave.tjaarda@smurfitwestrock.com |  |

‡ = Denotes attendance at meeting Spring 2025

- Denotes new subcommittee member on this list; previously added to subcommittee.

Registration List*

| BLRBAC Spring 2025 Meeting - FINAL TOTALS - Tuesday 4/8/25 12:00pm |  |  |
| --- | --- | --- |
| First Name | Last Name | Company |
| George | Pyszynski | 3S TEAM, LLC |
| Jake | Shelton | Acoustic Cleaning Systems |
| Todd | Harley | Acuren |
| David | Dunn | Acuren Inspection |
| Wayne | Grilliot | AF&PA |
| Scott | Markrof | Ahlstrom |
| Rickey | Bazelle | Alabama River Cellulose (GP) |
| Jeremy | Nicholson | Alabama River Cellulose (GP) |
| Tyler | Stanley | Alabama River Cellulose (GP) |
| Ben | Fredrick | Allnorth Americas |
| John | Hornsby | Andritz |
| Greg | Imig | Andritz |
| Mark | LeBel | ANDRITZ |
| Samuel | Miller | Andritz |
| Zachary | Payne | Andritz |
| Aaron | Rose | Andritz |
| Greg | Swayne | Andritz |
| Preston | Morgan | Andritz Inc |
| Paul | Ceravolo | Andritz Inc. |
| John | Phillips | ANDRITZ Inc. |
| Scott | Lowrie | Andritz, Inc. |
| Cameron | Davies | Aon |
| Bill | Castle | Applied Technical Services |
| Harrison | McLarty | AXA XL |
| Allen | Broadus | AXA XL Risk Consulting |
| James | Franks | AXA XL Risk Consulting |
| Tom | Edwards | B&W |
| John | DeFusco | Babcock & Wilcox |
| Greg | Sallee | Babcock & Wilcox |
| Evangelos | Townsend | Babcock & Wilcox |
| Laura | Nicol | Babcock and Wilcox |
| Matthew | Ackerman | Bama River Cellulose (Georgia Pacific) |
| Tim | Hicks | Billerud |
| Dean | Clay | BSI |
| Frank | Navojosky | BSI - Boiler Services and Inspection |
| Fred | Call | Buckman |
| Brent | Bourassa | Clearwater Paper |
| Ishaq | Jameel | Clyde industries |
| Daniel | Franco | Consultant |
| Daniel | Roddy | Core Refractory Systems |
| James | Biggs | Crenshaw Machine Systems |
| Juan | Reyes | Crenshaw Machine Systems |
| Jordan | Spicer | Diamond Power International Inc. - |
| Carlo | Tomassetti | DiVal Safety / CoreMAX FR |
| Oscar | Guevara | Domtar |
| Kolby | Stockton | Domtar |
| Gregory | Burns | Domtar Corporation |
| David | Avery | Domtar Paper |
| Herman | Haywood | Domtar Paper |
| Silas | Whitehead | Domtar Paper Company |
| Jesse | Worsham | Domtar Paper Company, LLC |
| Gerald “Trey” | Nail | E & E Tech |
| Matthew | Jones | E and E Tech |
| Ryan | Smith | E and E Tech |
| Oliver | Baumann | Ecolab |
| Don | Downey | Ecolab |
| Brad | Osborne | Electron Machine |
| CA | Vossberg | Electron Machine |
| Scott | Pettigrew | Enero Solutions |
| Jennifer | Sandstrom | Enero Solutions |
| Nicholas | Ferri | Environmental Energy Services |
| Christian | Steiner | Explosion Power GmbH |
| Andrew | DOrazio | Factory Mutual |
| Jeremy | Rader | Factory Mutual Insurance Company |
| Resham | Adhikari | FM |
| Andre | Beaulieu | FM |
| Francisco | Britt | FM |
| Neil | Chaudhuri | FM |
| Chris | Combs | FM |
| Scott | Crysel | FM |
| Josh | Fetting | FM |
| Derrick | Gossen | FM |
| Chris | Hovanec | FM |
| Kevin | Huelsbeck | FM |
| Steven | Kern | FM |
| Guy | Labonte | FM |
| Pedro | Marcello Godinho | FM |
| William | Matisak | FM |
| Paul | Murphy | FM |
| Jimmy | Onstead | FM |
| Matthew | Paine | FM |
| Daniel | Pope | FM |
| Nicholas | Quigley | FM |
| Maxime | Simard | FM |
| Jason | Sirros | FM |
| Kimberley | Yulo | FM |
| Thomas | Meehan | FM Global |
| Andy | Clement | FPS |
| Peter | Donahue | FPS |
| Yoram | Schaker | GE Steam Power Inc. |
| Dan | Cudmore | GE Vernova |
| John | Lewis | GE Vernova |
| Michael | Rushing | General Electric |
| Ethan | Blair | Georgia Pacific |
| JC | Browning | Georgia Pacific |
| Jake | Dowland | Georgia Pacific |
| Brent | Griffin | Georgia Pacific |
| Adam | Marickovich | Georgia Pacific |
| Tom | Meadows | Georgia Pacific |
| Steve | Morrison | Georgia Pacific |
| Robert | Orender | Georgia Pacific |
| John | Price | Georgia Pacific |
| Luke | Coutinho | Georgia Pacific LLC |
| Greg | Zavadoski | Georgia Pacific LLC |
| Chad | Harrod | Georgia-Pacific |
| Wes | Hill | Georgia-Pacific |
| Gregg | Lentz | Georgia-Pacific |
| Olli | Kujanpaa | GP |
| Bruce | Pease | Graphic Packaging International |
| Angelo | Porchetta | howe sound pulp and paper Domtar |
| Kevin | Phillips | Integrated Global Services |
| Vernon | Blackard | international paper |
| Derrick | Clarke | International Paper |
| Stephen | Cox | International Paper |
| David | Frazier | International Paper |
| Robert | Miller | International Paper |
| Paul | Peters | International Paper |
| Brian | Rawson | International Paper |
| Trevor | Murray | Irving Pulp and Paper |
| Matt | Glenn | Irving Pulp and Paper Ltd |
| Danny | Mott | Irving Pulp and Paper Ltd |
| Brendan | Dooley | J.D. Irving |
| Steve | Campbell | Jansen Combustion and Boiler Technologies, Inc. |
| Douglas | Giarde | Jansen Combustion and Boiler Technologies, Inc. |
| Mark | McCabe | Jansen Combustion and Boiler Technologies, Inc. |
| Jerrel Bobby | Johnston | Johnston Construction LLC |
| Shannon | McKenzie | Kadant Black Clawson LLC |
| Richard | Salliss | Keit Industrial Analytics |
| Thomas | DeBeer | LCK Consultants |
| Michael | Sweeney | Liquid Solids Control, Inc. |
| Christopher | Skorton | Liquid metal Industrial Solutions |
| Paul | Seefeld | Lundberg LLC |
| Glenn | Hanson | Metso |
| Rob | Richards | Metso USA Inc. |
| Stacy | Power | MidState SMS LLC |
| Roger | Lawton | Milhous |
| Frank | Crumpler | Nalco |
| Billy | Collett | National Boiler Service, Inc. |
| William | Burns | ND Paper |
| Joseph | King | ND Paper |
| Jason | Lewis | ND Paper |
| Dan | Robinson | ND Paper |
| Kurtis | Barnett | ND Paper Inc |
| Wayne | Bucher | Noram |
| Christian | Cote | Paragon Risk Engineering |
| Benjamin | Roberge | Paragon Risk Engineering |
| James | Dilworth | Pixelle Specialty Solutions |
| Anna | Racine | Pixelle Specialty Solutions |
| Tom | Przybylski | Power Specialists Assoc., Inc. |
| Vince | Barreto | Power Plus Cleaning Systems |
| Carl | Wise | Power Plus Cleaning Systems |
| David | Fuhrmann | Precision Reliability LLC |
| Logan | Baker | Process Barron |
| Derek | McCallum | Process Barron |
| Jennifer | Smith | Process Barron |
| Tripp | Whatley | Process Barron |
| Alex | Claverie | PSA |
| Mike | McGregor | Radian Chemicals |
| Rick | Baxter | RMR Mechanical, LLC |
| Mike | Bayse | RMR Mechanical, LLC |
| Kyle | Boucher | RMR Mechanical, LLC |
| Brook | Holland | RMR Mechanical, LLC |
| Jenny | Joyce | RMR Mechanical, LLC |
| Jed | Merritt | RMR Mechanical, LLC |
| Dylan | Price | RMR Mechanical, LLC |
| Donnie | Wilson | RMR Mechanical, LLC |
| Daniel | Albert | Rotork |
| Patrick | Buyck | Sappi |
| Benjiman | Ward | Sappi |
| David | Boudreau | Sappi Fine Paper |
| Bernie | Abramczyk | SEI-Group |
| Steve | Lessard | Sigma 7/Paragon Risk Engineering |
| Scott | Moyer | Smurf it Westrock |
| Kyra | Attridge | Smurfit WestRock |
| Christopher | Crocker | Smurfit Westrock |
| Robert | Edens | Smurfit Westrock |
| Brian | Hudson | Smurfit Westrock |
| Deshawn | Kraemer | Smurfit Westrock |
| Michael | Merino | Smurfit Westrock |
| Douglas | Murch | Smurfit Westrock |
| Evan | Saumer | Smurfit Westrock |
| Alarick | Tavares | Smurfit Westrock |
| David | Tjaarda | Smurfit Westrock |
| Randy | Tompkins | Smurfit Westrock |
| Scott | Holloway | Solenis |
| Jim | Meredeth | SOLENIS |
| David | Wolfanger | Solenis |
| Jeff | Armstrong | Solenis LLC |
| Mike | Bruce | Sylvamo |
| Nick | Folster | The Babcock & Wilcox Company |
| James | Monette | The Babcock & Wilcox Company |
| Frank | DeStefano | Thermax |
| David | DiCorpo | Vaisala |
| Ricky | Henderson | Vaisala Inc |
| Keijo | Pyörälä | Vaisala Oyj |
| Casey | Beirne | Valmet |
| Zackary | Fanelty | Valmet |
| Dave | Gadai | Valmet |
| Abby | George | Valmet |
| Rob | Goggins | Valmet |
| Sarah | Henke | Valmet |
| Daniel | Lishbrook | Valmet |
| Matthew | Sparks | Valmet |
| Cameron | Weir | Valmet |
| Jeremiah | Yoder | Valmet |
| Travis | Conner | Valmet Automation |
| Ronald Joseph | Reed | VALMET INC. |
| Neal | Powell | Valmet, Inc. |
| Timo | Karjunen | Varo Industrial Services Ltd |
| Jason | Beaudoin | WestRock |
| David | von Oepen | WestRock |
| Wade | Shirley | Westrock mahrt mil |
| Sammy | Wiggins | Westrock mahrt mil |

### MAIN COMMITTEE MEETING

- Introduction – (Gregory Burns – Chairman)

Good morning!  Welcome to the Spring 2025 BLRBAC Main Committee Meeting!  Thank you all for being here and participating this week.  This is our second meeting at the Hilton Hotel and I hope everyone found things to their satisfaction.  As this is our second meeting at the Hilton, and I think it went well maybe a little better than the Fall but I realize things are not perfect.  We will continue to work with the Hilton Hotel to close any gaps.  Please provide us feedback as to how your experience has been so we can improve any areas that are lacking.  I will be preparing a survey to be sent out so we can get feedback.  We had a good week with a lot of excellent participation, especially in our Sub Committee meetings, which were well attended.  BLRBAC has thrived over the years from its face-to-face interactions at these meetings.  A lot of discussions and exchange of good information.  We continue to build momentum on our BLRBAC meeting participation.  This week’s meeting had a very good turnout.  We had 213 members register.  Our average has been around 200-210.

With that we will carry on with our business.  The Main Committee Meeting is now officially open.  This meeting is being held in strict compliance with BLRBAC’s Anti-Trust Policy.

PLEASE REMEMBER THAT ALL BLRBAC MAIN AND SUBCOMMITTEE MEETINGS INCLUDING THIS SESSION ARE TO BE HELD IN STRICT COMPLAINCE WITH THE BLRBAC ANTITRUST POLICY.  DISCUSSIONS INVOLVING PRICE, PRICING POLICY, AND ANY RESTRAINT ON COMPETION ARE NOT ALLOWED DURING THESE MEETINGS.

I’ve reviewed the registration list and found that we have 19 Regular Member companies at this meeting and therefore, I am declaring that we have a quorum for today’s Main Committee meeting.

We will begin with some introductions from the executive committee members this morning.  We will introduce ourselves one-by-one.  Some of the faces are different than last fall. With Frank Navojosky retiring from International Paper the executive committee voted to move myself, Gregory Burns from vice chairman to Chairman, Dave Tjaarda to Vice Chair and placed Scott Moyer in as the operational representative to serve for the remainder of the term in accordance with the BLRBAC articles of association and bylaws.

I am Gregory Burns, I am the BLRBAC Chairman.  I am also the Director for Power, Recovery and Energy Optimization for Domtar Paper and I am a member of the ESP subcommittee.

2.0 Old Business (Gregory Burns)

ACCEPTANCE OF THE FALL2024 MEETING MINUTES –

With that we will move into old business and acceptance of the Fall 2024 meeting minutes. The Meeting Minutes for the Fall 2024 BLRBAC session have been posted on the BLRBAC web site.  The website is blrbac.net.  Does anyone else have comments or discussion regarding the Fall 2024 meeting minutes as posted?

Can I get a motion to accept the Minutes as posted?  We have a motion.  Second?  All in favor of accepting the minutes as posted?  Anybody opposed?   Thank You! The Fall 2024 Meeting Minutes have been approved.  Is there any other old business that we need to bring to light?

3.0 New Business Report (Daniel Franco)

The Executive Committee met to discuss new member applications.  No new applications received and are Rebuilding the old list for voting and alternate representatives from member Companies.

4.0 Executive Committee Report (Gregory Burns)

The executive committee met yesterday in a closed session.  We discussed the budget as Brad will detail next.  Basically, the financial position of BLRBAC is sound.  We spent a lot of time discussing the move to the Hilton and the issues that have come to our attention and as I said earlier a survey will be sent out to all attendees to provide feedback.  I think we are all in agreement to hold the Fall meeting here at the Hilton but that there is work to be done to make the process smoother and remove the bugs that have plagued those trying to register.

The executive committee also voted to move the Instrumentation Guidelines to a vote by the membership.  We have John Browning review those changes during the Instrumentation Subcommittees presentation prior to a full vote by the membership.

5.0 Treasurer’s Report Brad Osborne

As of April 8, 2024, the balance in our checking account was $122,824.99. Our estimated gross meeting revenue for this meeting is $106.875. Our estimated expenses for the Spring meeting are 70,000 to the hotel and $26,000 to Metro, there will also be a few admin fees we need to account for such as legal reserves and secretarial work. We have prepaid $10,000 to the hotel before the meeting, I expect a hotel balance of approximately $60,000, but we should add approximately $7,000 to our checking account after the Spring meeting. This would have the account at $129,000 before the Fall 2025 meeting. This would complete our goal for the account to carry a balance of one full meeting plus a small reserve. The members booking though our hotel registration link was completed but will need to continue to keep our hotel cost in check. We will be in the Hilton for the Fall. The committee continues to evaluate the bank balance and conference cost. If meetings continue at the Hilton, maintaining a bank balance that accommodate any unforeseen expenses, and the prepayment of the conference is necessary.

We had 201 advance registrations and there were 15 at door registrations and three cancelled for a total of 213. Participation was down from the fall but increased from Spring 2024. There were 23 attendees from outside the US. With 17 people from Canada, 2 UK, 2 from Finland, one person from Switzerland, and one person from Columbia.

| Balance as of April 5th, 2025 | $122,824.99 |
| --- | --- |
| Estimated Spring Gross Meeting Revenue | $ 106,875 |
| Estimated Expenses for Spring | $99,800 |
| Fall Meeting Hilton and AV | $ 70,000.00 |
| Metroconnections | $26,000 |
| ESP | $ 3,000.00 |
| Office | $ 800.00 |
| Other Expenses from Budget | $5,000 |
| Total | $92,800 |
| Estimated Meeting Revenue | $7,075 |
| Prepayment | $10,000 |
| Estimated EOM Checking Balance | $ 129,899 |

6.0 Secretary’s Report (Daniel Franco)

MEMBER COMPANY ACQUISITION

MEMBERSHIP COMPANY STATUS CHANGES – None at this time.

{Secretary’s Note:  The Company Membership List posted on the BLRBAC website may be  out of date and  not reflecting all the mergers, acquisitions, and name changes that have occurred.  Anyone who sees something that needs changing should bring it to the attention of the BLRBAC Chairman and Secretary.

7.0 SUBCOMMITTEE REPORTS

7.1	AUXILIARY FUEL – Tom DeBeer – Chairman

BLRBAC Safe Firing of Auxiliary Fuels Subcommittee

April 7, 2025, Meeting

The Aux fuels committee met in the morning and the afternoon.

9:40- 11:45 in open session. Due to lack of quorum a work group meeting has held.

The BLRBAC anti-trust statement was read and revied.

Two guests and Three committee members were present.

13:00 – 15:30 in closed session

The BLRBAC anti-trust statement was read and revied.

Zero guests and five out of eight committee members were present.

Bruce Knowlen Subcommittee Chair retired from International Paper with over 30 years of service to the Safe Firing of Auxiliary Fuel Committee.  His knowledge, wisdom and guidance will be missed. The committee wish Bruce all the best in his well-deserved retirement.

The committee reviewed changes proposed to the document for over twenty figures and over ten tables.

Each item was reviewed and voted on by the committee. All proposed changes were approved unanimously. The committee will finalize the changes to the document at the fall meeting and will submit it to the executive committee for approval.

7.2	ESP SUBCOMMITTEE – Frank Navojosky – Chairman

ESP subcommittee meeting report out 4/9/25

ESP SUBCOMMITTEE REPORT – Frank Navojosky – BSI (Boiler Services & Inspection LLC)

Closed ESP subcommittee meeting 4/7/25

The closed meeting was called to order at 8:00 AM Monday 4/7/25 by ESP Chairman Frank Navojosky and the Antitrust Slide was read

Membership attendance

We had 12 members present out of 13 active members with 1 absent (Mike Bates of WCBLRBAC).

Regular Business

- Reviewed and Approved the Previous Minutes – October 7th, 2024

- Reviewed the 20 Assigned US and Canada Incidents reported and 1 International incident

- Discussed proposal of changes to our latest ESP Guideline Document.

- Rapid Drain valve - Rotork configuration – Adjusted wording based on ISC feedback to send to Executive committee for approval.

- ESP Logic – Air changes desired on ESP – Working on logic block and document wording to allow mills the flexibility to address the critical functions of both cutting combustion air off to reduce bed activity after ESP and providing purge airflow to remove combustibles. This is needed as a result of various port design elevations and air operating strategies.

- Mike Bruce and Frank Navojosky have volunteered to continue the updating of the BLRBAC historical lessons learned document on the website.

- We have encouraged reports of near misses/smelt rushes with DT’s. We had 1 report this session to discuss. It was classified as an explosion due to damaged auxiliary equipment.

- Dean updated the BLRBAC incident report document to make it clearer for reporting all DT incidents not just explosions. It was approved and will be placed on the website for use.

New Business

Scott Moyer was selected as the new Committee Vice Chair.

Meeting was Adjourned at approximately 3:30 PM 4/7/25

Open ESP subcommittee meeting 4/8/25

The open meeting session was called to order 4/8/25 by ESP Chairman Frank Navojosky - BSI at approximately 8:30 AM

START OF OPEN ESP COMMITTEE MEETING

1.0 Introduction – (Frank Navojosky BSI – ESP Subcommittee Chair)

Good morning.

Welcome to the Fall 2024 BLRBAC Open ESP Session.  The Fall Session is now officially open.

My name is Frank Navojosky of BSI (Boiler Services and Inspection), and I am the Chair of this ESP Subcommittee.

Some of you also remember that I was voted in as BLRBAC Executive Chair. But due to our bylaws, the Chairman position must be held by a member company. Member companies are: Operating companies, Recovery Boiler Manufacturers and Insurance companies. All other members are Associate members.

Due to my recent retirement from International Paper Company, I am no longer with a member operating company and therefore stepped down from the Executive Chair role. I may have the shortest tenure in the history of BLRBAC.

PLEASE REMEMBER THAT ALL BLRBAC MAIN AND SUBCOMMITTEE MEETINGS INCLUDING THIS SESSION ARE TO BE HELD IN STRICT COMPLAINCE WITH THE BLRBAC ANTITRUST POLICY. DISCUSSIONS INVOLVING PRICE, PRICING POLICY AND ANY RESTRAINT ON COMPETION ARE NOT ALLOWED.

At this point, I would like to have the ESP Subcommittee introduce themselves.

We have one member absent, Mike Bates of Western Canada BLRBAC.

With that, we will now begin the ESP subcommittee open session with discussion of the first incident. The Panel will present the Economizer and Superheater incidents. For these incidents, if there is someone from the mill that is present, who can answer any questions, please speak up.

For other incidents, if there is a person from the mill that is present, who would like to present the incident, please step to the microphone when asked. A reminder: Refrain from taking photos or screen shots. Material appropriate for sharing will be published in the meeting minutes on the BLRBAC website.

(See Appendix I – Incident List and Appendix II ESP Presentation)

7.3	 FIRE PROTECTION IN DIRECT CONTACT EVAPORATORS- Stephen Cox– Chairman

Did not meet in the Spring 2025

7.4	INSTRUMENTATION – John Browning – Chairman

SPRING 2025 BLRBAC INSTRUMENTATION SUBCOMMITEE MEETING

April 7, 2025, J.C. Browning, Chairman

Notes from C.A. Vossberg

8:00am EDT, meeting called to order

- BLRBAC Antitrust policy reviewed.

- Membership roll call, 9 members of 17, enough for a quorum. Had 17 visitors

- Introduction of members and guests.

- Reviewed minutes from Fall of 2024, motion was made with a second to approve.

- Had discussion about primary and alternate means for rapid drain valves. Discussed and reviewed details concerning proper configuration for the various Rotork MK1, 2, and 3 valves.

Daniel Albert from Rotorq reviewed Rotorq IQ documentation for BLRBAC applications.  A change was made for settings on the Feedwater Valve configuration.  Motion made and seconded to send to the Executive Committee, for posting. This has taken awhile (years) to get done.

- Discussion about the path forward, as a sub-committee, for making timely updates to update ISC Recommended Practice document.

We have for years tried to reconcile the ISC document with all of the other recommended practices with mixed results due to many of the members retiring or leaving.

I will be setting up a monthly TEAMS call and start reconciling sections. Each meeting, we will submit sections that have been updated for posting to our current document.

Dave Boudreau reviewed section G of our document he prepared to show all on the committee the format we were using.

The format includes: “First Out Date” and “Research Notes” columns have been added.  Changes have been added in red color with other subcommittee documents referenced.  Additional changes need to be made since some of the practices have changed.

- Open roundtable: what issues does this subcommittee need to be addressing.  Discussion about the following subjects was discussed:

  - Redundant measurement technology for critical measurements especially during start-up. Reliability contributes to safety.

  - Combustion analyzers (CO vs. Combustibles vs. O2)

  - Airflows, tramp air, furnace pressures, etc.

  - Class I (required) verses Class 2 (recommended) in our document.

  - Dissolving tank density and agitation:  Some operating companies have internal permissive requirements above and beyond BLRBAC recommendations, specifically in regard to minimum agitation.

  - Instrumentation field device calibration and functional checks.  Critical instruments versus informational.

  - Switches verses transmitters. Transmitters can be trended, can see if active / functional, and provide process insight that switches cannot.

  - The importance of performing full functional tests.

  - MFT nuisance trips: relays that have failed to change states, terminal connections of field devices that have loosened over time, etc.  PM’s need to be in place to recognize and prevent.

  - Importance of supervising instrumentation contractors to ensure proper maintenance is being performed during shut-downs and equipment is ready to be returned to service after maintenance is performed.

  - Existing base of Rotork IQ valves that may not be properly configured.

For mills with IQ Rotork valves in service: Recommend contacting Rotork Daniel  Albert, (Rotork product manager for pulp and paper) or Rotork Site service team) for on-site review of installations. When ordering Rotork valves for recovery boilers, customers must state that it is intended for BLRBAC applications.

11:20am EDT, Lunch Break

1:00pm EDT, Afternoon session

9 committee members and 3 visitors

- Open discussion about the following:

  - Review of Rotorq discussion from morning session and real-world experiences and potential failure scenarios.

  - Discussion about Contractors performing shut-down calibration of instruments.

  - Green liquor dissolving tank density measurement.  Maintaining constant density (and temperature) control helps in minimizing scaling in the pipeline.  Automated Titration instruments require regular maintenance to remain in service.  Past experiences with real-world problems regarding dissolving tank operation and measurement.

  - Casual discussion about various topics relating to BLRBAC.

    - Has the possibility of moving BLRBAC from Mon-Wed to Tue-Thurs?

1:50pm EDT Meeting adjourned

7.5	MATERIAL & WELDING – Laura Nicol – Chairman

MATERIALS & WELDING Subcommittee Meeting REPORT

The Materials and Welding (M&W) Subcommittee met in Open Session on Monday morning, April 7, 2025.

The meeting was opened at 8:01 am with a review of the BLRBAC Anti-Trust Statement.

Attendance

Nine (9) members and one (1) voting alternates out of eleven (11) attended. There were two (2) non-voting alternates and seventeen (17) guests.

- Added William (Bill) Burns of ND Paper

Discussions

- Opened meeting with a Review of the BLRBAC Anti-trust Statement.

- Introduction of attendees

- Reviewed minutes from last meeting and approved.

- Review the updated Material and Welding Guidelines

  - Published for general review at https://blrbac.net/documents-for-review-comment/

  - A review by members found additional information would be helpful in a couple of sections

    - General forward now mentions backing rings but is not discussed elsewhere in the document. May require a new section

      - Action Item: Maxime Simard (FM) was requested to help draft language.

    - A new sentence was added to Section 3.3 about repairs of pressure boundary materials (weld build up) in this revision cycle.

      - Action Item: need to add additional information in Section 4.3. Laura Nicol of B&W to add pictures from NBS report on burn through. NBS has agreed to the use of their pictures.

- Presentation on Grade T24 (CC 2540-1) Material Experience – Bill Burns of ND Paper

  - 2.5Cr-1Mo-V-B-Ti

  - Reviewed ASME Section I Code Case 2540

  - Discussed using a higher preheat temperature (400F vs. 300F)

- Reviewed additional agenda items:

  - Deciding factors on when to make tube weld repair – item was covered by adding the new sentence in Section 3.3.

    - Action Item: In October 2025, review Laura Nicol’s modifications to Section 4.3.

  - Neutral axis fatigue cracking in bends

    - Discussion from Mark LeBel of Andritz: Stress Assisted Corrosion (SAC) can occur in bend if there is enough residual stress and the water chemistry is bad enough. Background: a package boiler at a paper milled suffered a failure at a bend.

    - Action Item: Determine if this information should be added, and if so, where?

  - Discuss issues with beveling weld overlaid tubes that have been cut with an abrasive disc (metabo)

    - Bill Burns (ND Paper): use a Z tool to remove weld overlay and expose the OD of the carbon steel tube

      - Prefers to leave ~1/8” carbon steel land to prevent overlay contamination

      - 825 is harder to peel back than stainless or 625

    - Bobby Johnston (Johnston Construction): peel back is harder on Weld Overlay (WOL) than composite tubes

      - Will use a burr bit to clean up the peel back

- Discussion on cracking at a composite floor to carbon steel membrane bar welds.

  - Maxime Simard (FM) has a customer dealing with this issue

  - Mark LeBel (Andritz): this was a known issue in the 1990’s. Oak Ridge National Laboratories did extensive work on 304L.

    - Action Item: Locate old ORNL reports

  - Bill Burns (ND Paper): Cracking can depend on how hot the lower furnace is (air input). Cracking susceptibility on temperature goes: carbon steel to stainless to 625/825

- Discussion on tube rolling hardness.

  - Yes, there is such a thing as too soft

  - Most agreed that SA-210 A1 should have hardness range in 72 -75 range to allow easy rolling.

    - Paper mills need to request extra heat treatment of rolled tubes to ensure this hardness range is met

  - Do not go down below 69 HRB or the ASME minimum tensile properties requirements will be violated

  - Showed the hardness to tensile table located in ASTM A370.

    - Action Item: Laura Nicol (B&W) to develop presentation for Fall 2025

- Discussion on training information and resources

  - Action Item: Mike Rushing has been requested to develop a presentation for Fall 2025.

    - Discussed training sessions put on by ASME Code

Meeting adjourned at 10:06 am

7.6    PERSONNEL SAFETY – Ben Ward – Chairman

Personnel Safety Sub-committee

Spring 2025 Meeting Minutes 4-9-25

Committee chair Ben Ward

The Personnel Safety Sub-committee met in an "open” session at 8 am on Monday, April 7, 2025, and in a closed session at 1 pm as well.   There were a total of approximately 45 attendees at the meeting, 5 members of the committee were present during the open meeting and 8 committee members attendance at the closed meeting.

Open Meeting started 0800.

Representation at our meeting by regular members and guests included

- 2 original equipment manufacturers (Andritz, and Valmet)

- 6 Product/Service Providers (Gore, Bodman Services, Varo industrial services, Kadent, Teknik, 3S)

- AF&PA and insurance company representatives

- Operating company representation included 24 people from 10 different operating companies, ND Paper, Ahlstrom, Domtar, Georgia-Pacific, Pixelle, SAPPI NA, International Paper, GPI ,Clearwater and Smurfit WestRock.

- We had at least 6 engaged operators present.

The BLRBAC anti-trust statement was read.  Individuals introduced themselves and a sign-in sheet was passed around for a record of attendance and contact information.

The minutes of the last meeting (October 2024) were reviewed and accepted.

Main Topics of discussion

  - Safety Moment shared – “safety starts with me” ~ “Care enough to act” – Ben Ward

  - Safety incident share

    - Sappi – spout and port rodding ergonomics – shared training improvement – use of occupational therapist to review video of operators and developed document to improve training for proper ergonomics

    - Clearwater paper – Ladders safety related incidents resulting in falls – unmanaged ladders in remote areas of the plant

    - Domtar – hand caught in nip on conveyor trying to clear plug with a tool – resulting in significant injuries - focused on improved guarding audit – installation of guarding reduction of overall risk.

    - Good open conversation on new employee challenges and rapid promotion through line of progression – discussed improved SOPs and check lists – challenges with the experience gap

    - Brief discussion on Hexavalent chromium – what people are seeing what proactive measure are taken place – discussed education approach what to look for

    - Discussed use of personnel air monitoring devices – what areas are required

    - Entry protocols check lists after water wash

    - Safety improvement projects – example from Cloquet spout shield

  - Valmet -  Smelt protection garment update, smelt head protection product and update on multi-Haz garment (focused on steam protection testing). – Nick Dellinger and Cameron Weir

  - CoreMAX FR – Carlo Tomasetti

  - Johan Engvall – with Teknik Support presented their automatic spout cleaner – currently 3-4 installations in Sweeden

  - Spring grove still open to host visits to view Valmet robot installation.

  - Discussed plan to review the personnel safety guidance document

  - Asked for potential topics for future meetings

    - “new” operators as well as managers and challenges with rapid advancement

    - Questions about leak detection – training and procedures

      - TAPPI TIP for leak detection

    - Review and move from people centric to system centric

- The meeting ended at 11:30.

- Closed meeting began 1:00 – 8 members present

Sam Miller

Jake Dowland

Ben Ward

Steve Morrison

Zach Payne

Francisco Britt

Mathew Glenn

Brook Holland

- Reviewed morning session

- Discussed potential topics for next year

  - Continued encouragement to share personnel safety incidents and near misses

  - Challenges with the experience gap

- Began Review of guidance document and begin updating

  - Made it through page 15/72 of the document

- Member contact info update

| Jake Dowland‡ Georgia Pacific Tel: (229) 202-4188 Jake.dowland@gapac.com | Sam Miller‡ Andritz 5405 Windward Parkway Suite 100W Alpharetta, GA 30004-3894 Tel: (678) 533-9431 Samuel.miller@andritz.com |
| --- | --- |

Will set up a method to share in between meetings

There were no requests for clarification or interpretation in the last six months.

In closing, we are always welcome to new committee members who can participate in any capacity even if you can only attend meeting intermittently.

7.7    PUBLICITY & NEWS – Matt Paine– Chairman

Report here from the publicity subcommittee….

BLRBAC continues to post meeting notices on industry website event calendars such as TAPPI and Paper Age.

Kind Regards,
Matt

Matt Paine | Staff Engineering Specialist | Chief Engineer’s Group, Specialty Industries
FM | 270 Central Ave. |  Johnston, RI 02919  | Office 401 415 2274 | Mobile 503 319 1815

7.8	 SAFE FIRING OF BLACK LIQUOR – Vernon Blackard– Chairman

BLRBAC SFBL MEETING DRAFT MINUTES –

April 2025

Monday  April  7th -  8:30  am – 11:30 am

8:30 am	--Noon	Safe Firing of Black Liquor Subcommittee – (CLOSED)

1 pm to 4 pm	Safe Firing of Black Liquor Subcommittee - (OPEN)

# Proposed Agenda:

- Open the meetings.  Both Closed and Open.

- Reviewed BLRBAC Anti Trust statement.  Both closed and open meeting.

- Introduce members and guests. 18 members in closed and approx. 56 members/ guests in open.

- Review and approve the Fall 2024 minutes.  Approved

- Review any open items brought up to the subcommittee before the Spring 2025 Meeting.

- Continue new revisions after our Fall 2023 document was approved and posted.

- Review Spring 2025 Draft:

Ch 3.5 LTL Logic…consider closing feedwater valve on ANY high FP or low DL event.

Do all mills use tube leak check sheet with LTL logic?

Not much response…

Consider interlock on any low drum trip.

Ch 9.15 Spout leaks.  Consider changing spout if cooling water off over 24 hours. Immediate attention.  Close off water to spout and plug immediately after any loss of cooling water flow.

Ch 10.1 DT Plugged spouts – Black out conditions.  If you cannot get your primary ports open within 48 hours (immediate attention) then do orderly shutdown, cool bed, and wash out the furnace and clear ports.

How many mills have Flush mounted vs inserted?

24 or 48 hours to shut it down? Next outage?

Losing the seal at the furnace is the concern that needs to be considered.

Discussion about a rod in the spout with a small leak.

Discussion about how long to wait after plugging to go in the area. To adjust shatter spray? Broken bracket?

More than xx plugged primary ports? Spouts might acted erratic. Damage has been witnessed. Burning casting.

Ch 10.2 DT design- Item 4 have two density devices , Item 5 have two level devices.

Good idea, not expensive and much safer.

Ch 10.3 DT Operation – item 5 on loss of DT primary agitator. Do not run over 48 hours with back up agitation unless OEM approval.  Steam spargers plug after a while so should be checked every week. What is the definition of an adequate back up for primary agitatiion? Why 48 hours? Then what?  Should this be removed? No time?  Require immediate attention? Doe it depend on sample location? Should each mill be required to get the OEM suggestion of what is adequate back up?

Should individual modeling for each SDT be done?

Discussion about circulation modeling in a SDT when 1 of 3 agitators goes down.

- Items brought up since Fall 2024 meeting:

- Tim Hicks discussion.

1-minimum hearth burners required for “stable firing”.

As solids come up less burners are needed, and also when coming down with the boiler.

Exposed or covered floor changes the % of MCR required to have the proper heat in lower furnace.

In some cases even 10% is enough. 70% solids…

Looking for a guideline of what is safe?

If the steam flow drops below 30% but at least one aux burner is in it’ll be a liquor divert but not a MFT.

Operators need to pay stricter attention when introducing liquor to be sure it is burning. Natural gas increases the challenge to get the % of MCR up and get the heat down in the lower in the furnace.

Operator Initiated MFT’s?  Is shutting off the primary air a good idea, or will it cause more operational and safety issues?

Is tertiary air needed for a boiler purge? Prove all FD fans and some flow thru all windboxes with damper open to some extent.

2- MFT what actions should be taken during an MFT.

- Continue discussions from Spring 2024 meeting (Refer to minutes).  CONTINUE DISCUSSION FOR HIGH SOLIDS FIRING WITH SARAH INPUT.  Some consider external heating of liquor pipes to prevent plugging on trips.  Continue discussion next meeting.

Black liquor divert changes:

Specifically for high solids firing.

What if 1 of the 2 valves doesn’t reach its closed limit?

Right now we shut off a valve and pump.

Pressurized tanks to accept the high solids liquor form the lines to keep them from plugging. 80-83% solids increases the problem.

- DT incidents to be reviewed:

Reviewed Mansfield incident. 3rd time something similar has happened at this mill recently. But not the same spout or same boiler. Rear wall slag/debris fell off in front of spout. Smelt pool came loose?

Sulfidity should be added to the BLRBAC form.

The question of could the operation of the scrubber system cause this, was brought up.

Classified as a SDT explosion.

Rumford Me mill ND:

Missing refractory at bottom of spout caused the issue.

Filling smelt box with refract, contractors may have left an air pocket in the refract.

Normally 12 months, but tried going 18 months.

Good idea to inspect this area during or right after the water wash.

- Mike Bruce SYLVALMO Comments put into draft document.  Time to run after PAP black out and time to run after spout cooling water shut off.

Need more engineering around SDT’s.

- AFPA DT VENT STUDY – UPDATE ON STATUS

Three type of DT venting design requirements.  Normal at full liquor firing rate, smelt rush at normal firing rate, DT explosion venting when percussions occur.

5’6” for shatter jet space

43” of freeboard from surface to bottom of overflow line.

- DT FUNCTIONAL TESTING – UPDATE ON STATUS.

One mill uses air to cool the shaft of the DT agitators rather than water.

All should make sure they can isolate all water to the DT from a safe distance.

Homework:

GETTING OEMS TO DESIGN OVERFLOW FOR MMLBDS BL/DAY BASIS WITH PROCEDURES.

WHAT DO OEMS RECOMMEND FOR VAPOR SPACE ABOVE BOTTOM OF DT OVERFLOW?  43”

WHAT DO OEMS RECOMMEND FOR SMELT SHATTERING SPACE ABOVE BOTTOM OF DT OVERFLOW?

Sam presented.

Agitator diameter added to the CL of the agitator should be ‘0’ level of the tank.

Main concern is the geometry of the shatter jet.

Worst case scenario should be considered when doing the engineering.

Have all numbers available to any new supplier of spouts if changing.

DT Overflow should be sealed to prevent tramp air short circuiting to the scrubber fan.

How are we handling loss of weakwash and putting firewater or millwater on?  Emergency procedure addresses this?  How much do you turn on water, and do you continue to check baume?

- Open item discussion from members.

- Any new items will be discussed:

- Other functional tests on DT.   Check water sources off on crystallization event.

Shut off agitators and all water sources.

Hood wash water isolation

Peter says there doesn’t seem to be anything in out document diagrams to address isolating waste streams during a purge. In the liquor, not the combustion air.

- Open discussion from guests

- Guest questions?

- Explosion videos…Will share any submitted.  Have IP Power point of RB history of explosions (share visual only.  No copies or files shared).

- Close meetings as needed (closed and open).

Thanks, Vernon Blackard of IP.

7.9 WASTE STREAMS - Paul Seefeld– Chairman

Did not meet in the Spring 2025 Meeting

7.10	WATER TREATMENT – Tom Przybylski – Chairman

## Spring 2025 Meeting Attendees:

| ## Tom Przybylski/PSA ## Frank Destefano/3D ## Michael Bayse/Bodman ## Dave Tjaarda/Smurfit WestRock ## Tom Meehan/Factory Mutual ## Frank Crumpler/Nalco ## Plus 10 guests | ## Fred Call/Buckman ## Don Downey/Purolite ## Trevor Murray/Iriving Pulp ## Rick Baxter/RMR Mechanical ## Jeff Armstrong/Solenis |
| --- | --- |

- The water treatment subcommittee met in open session for morning and afternoon sessions with 11 of 14 subcommittee members in attendance.  There were 10 guests.

- The session started with a review of the BLRBAC antitrust statement.

- Meeting minutes from last spring were approved.

- Jeff Armstrong from Solenis was approved as the new representative from Solenis.

- The morning session started with a final review of testing and sampling document.

  - Numerous edits were made for readability and clarity.

  - A discussion about the need for adherence to temperature requirements ensued for conductivity constraints.  Specifically, is 25°C only important for low conductivity water, or would it apply to boiler water that has higher conductivity.  We reviewed pertinent ASME documents and discussed internally before striking the conductivity stipulations from this recommendation.

  - There was a question about steam sampling.  Where is isokinetic sampling necessary and how necessary is it?  We also had discussions about when/where to condense a steam sample.  We reviewed our existing guidance and opted to make no changes.

  - A question arose regarding whether there were sufficient ESOPs in this testing and sampling document.  Since this portion of the guidelines cover technique more than specific parameters that are out of bounds, we agreed that there were no additional ESOPs warranted in this section, aside from the addition of an ESOP for a lack of water testing reagents.

  - We added some comments about consideration for failure modes on critical instrumentation and what happens when an instrument goes outside of its design range.

  - There were two references to testing every shift.  We agreed that shifts vary by facility and opted to strike references to shift-testing.

  - We added some recommendations about following MOCs and jumper policies for critical instruments.

  - We removed an SOP about copper testing as it did not apply to the content of this section.

- Following lunch, we started the make-up water section.  In discussing bounds, we felt it was better to rename this the deionization section.

- Once a quorum returned to the meeting, we returned to the Testing and Sampling Document and voted to approve this for submission to the executive committee.

- We returned to the deionization section following the vote.

  - Boundaries and variations from a typical system were debated.

  - The subcommittee decided that the scope of this section should only include typical demineralizer and RO systems.

    - A rough outline of the section was assembled.

    - Brainstorming around failures, inspection, and monitoring generated lists of items that will be detailed in a future session.

- We adjourned at 3:20PM

- 8.0	AMERICAN FOREST & PAPER ASOCIATION RECOVERY BOILER REPORT – Wayne Grilliot - (See Appendix III – Slide Presentation)

The American Forest & Paper Association (AF&PA) Recovery Boiler Program was established in 1974 to help identify the root cause of recovery boiler critical incidents and explosions.  The AF&PA Recovery Boiler Program assists companies in improving the safety, integrity, and reliability of recovery boiler operations.  Recovery Boiler Program membership is open to all companies that operate recovery boilers.  Program activities are funded by member company dues.

The Recovery Boiler Program is under the direction of a Steering Committee which includes Stephen Cox (International Paper), Jeff Wagoner (International Paper), Greg Burns (Domtar) and Wes Hill (Georgia-Pacific).  The Steering Committee sets Program priorities based on Member Company Input, BLRBAC Incidents, and Industry Needs.

The Recovery Boiler Program provides a forum for companies to develop information to help evaluate Safe Operating Procedures, Organization and Training, Maintenance Programs, Specifications and Construction, and Research & Development Programs.  Documents developed by the Program include Reference Manuals, Audit Guidelines, Best Practices, Training Aids, Checklists, Textbooks, and Studies.  The Program sponsors R&D projects for Safety Improvements and Process Improvements.  This helps drive improvements in Safety, Operations, Maintenance, and Recovery Boiler Integrity.

Available documents on the AF&PA Recovery Boiler Website include Publications, Studies, Training Aids, Standards, and General Program Information.

AF&PA Recovery Boiler Program Website:

http://www.afandpa.org/our-industry/recovery-boiler-program

9.0    TAPPI ENERGY, RECOVERY, RECAUST (ERR) Committee REPORT – ERR Committee Daniel Franco

Daniel Franco

ERR Committee Vice Chair

2025 – 04 – 09

Recovery and Power Boiler Subcommittee

Ray Reno

Water Treatment Subcommittee

Fred Call

Lime Kiln & Recaust Subcommittee

Wei Ren Nikolai De Martini

Energy Subcommittee

Ben Bunner

ERR Steering & Main Committee

TAPPI Engineering

Division

Chair: Wei Ren, FPInnovations

Vice Chair: Daniel Franco, Smurfit Kappa

Technical Program Chair: Alexander Moline, Domtar

TIP Coordinator: Ben Bunner, Andritz

This committee provides a forum to collect information and disseminate the information as a guideline for energy management, sharing ideas on conserving energy, and increasing efficiency. We publish Technical Information Papers (TIPs). We focus on pulp and paper mills and power plants in areas of energy management and energy consumption, including electrical, steam, condensate and efficient heat exchange.

Chair: Ray Reno, Volodyne LLC

The objective of this subcommittee is to develop and disseminate information and provide best practice guidelines related to the design and operation of recovery boilers, liquor evaporators, non- condensable gas systems, and related equipment. As well as to develop and disseminate information relating to steam generation from fossil or refusable fuels, either purchased or from on-site sources.

Chair: Fred Call, Buckman

The subcommittee aims to develop and disseminate information relating to the management of water quality throughout the power plant cycle. This includes the management of water supplies, boiler feedwater, condensate, cooling water, and industrial cleaning.

Chair: Ben Bunner, Andritz

The objective of the subcommittee is to develop and disseminate information relating to design, application, and operations in areas of power generation drive equipment’ energy policies affecting price and availability; power plant conceptual thermal cycle; and economical and effective energy management technology.

Chair: Wei Ren, FPInnovations

Chair: Nikolai De Martini, University of Toronto

The committee will focus on the design and operation of kilns and causticizing equipment in the pulp and paper industry. The goal will be to identify critical needs and develop pathways to increase understanding in key areas to help the industry to meet its goals in manufacturing efficiency and productivity. The committee will promote ongoing collaboration and alignment of industry owners and operators, equipment suppliers, and research organizations.

- Minneapolis, MN | May 4 – May 7, 2025

- New Program Format - Topics

  - Equipment, Processes & Operations

  - Emerging Technologies & Methodologies

  - Corporate Citizenship, Sustainability & Environmental Impact

  - Innovative Technology for Products & Processes

  - Talent Development, Safety & Best Practices

  - Pulp & Fiber Innovations, Alternative Materials and Applications

- Schedule to be determined due to changes to TAPPI conference schedule

- 2025 Spring Meeting to be hosted at TAPPICON

- 2025 Fall Meeting to be hosted after BLRBAC (TBD)

TIPs contain specialized information (e.g., data, software, calculations) used in the manufacture, evaluation and description of pulp, paper, and related products.

TIPs may contain testing procedures or methods used to evaluate equipment but do not contain pulp and paper testing procedures or methods.

- Recovery boiler soot blowers: practical guidelines

- Key to successful chemical cleaning of boilers

- Evaluating reverse osmosis for treating makeup to the boiler feedwater in a pulp and paper mill

- Guidelines for replacement of generating bank tubes with expanded joints in two-drum boilers

- Water treatment-related opportunities for energy conservation in a paper mill powerhouse

- Energy checklist: pulp mill

- Nitrogen oxide emissions control from biomass and kraft recovery boilers in the pulp and paper industry

- Best practice for recovery boiler inspection (optimizing inspection scope)

- Explanation of recovery boiler leak indications

# HOPE YOU CAN MAKE IT TO TAPPICON IN MINNEAPOLIS

THANK YOU

10.0   WESTERN CANADA BLRBAC REPORT  -  No report

11.0   ACTIVITIES OUTSIDE NORTH AMERICA REPORTS  Finish Recovery Boiler Committee - Timo Krjunen

12.0   OPERATING PROBLEMS SESSION REPORT – David Tjaarda

The session began at 1:00 PM on Tuesday April 8th, 2025 and was facilitated by Dave Tjaarda of Smurfit Westrock, Vice Chair of the BLRBAC Executive Committee.

There were 37 questions submitted in writing and 2 from the floor for a total of 39 questions.  We were able to share and talk through all the questions. The questions were related to the following topics:

- Hexavalent chrome, are folks inspecting for it, where is it being found, have the sources been identified

- Manual blow down, still done, frequency

- Emissions related to CNCGs & LVHCs, in particular SO2 emissions

- Smelt spout refractory failure, how common / frequent, alternative new refractory materials being developed

- Sodium analyzers, installation, reliability

- Top of nose arch seal box attachment inspection

- Cascade evaporator automated response to drum stopping, fire suppression and boiler MFT

- Feedwater steam drum inlet line thermal liner, leaks and maintenance of

- Long flow panel economizer, weld repair vs. dutchman vs. tube plugging

- Composite to carbon weld line corrosion above the weld line, exposure temperature & sulfidity impacts on corrosion rate

- Smelt Dissolving tank high density EOPs, specify density at which boiler is MFT’d

- Use in Nalco Corrosion Stress Monitoring in place of DO meter, use for closed loop control

- Recovery boiler dry out, use of air heaters vs. auxiliary fuel, dry out duration & outage duration when needed

- Troubleshooting tools used by operators, IR guns (attach to phone), acoustic devices / cameras, vibration pens, etc.

- Smelt Dissolving tank vent explosion damper safety

- Liquor header flushing

- Methanol firing in recovery boiler, mixed into liquor vs. independent burner

- Liquor gun ports safety, gates and barriers to keep folks out of the line of fire while allowing reasonable egress

- Smelt Dissolving tank agitators, brands used, problems, maintenance

- Steam valves, cast vs. forged, ASME specification

- Sootblowers, branch vs. individual blower isolation valves

- Mill return condensate treatment, polishers, cartridge filters, magnetic filters, chemical

- Superheater vents, flow indications, positioners on control valves, means to ensure tubes are clear

- Steam flow meters, type used, calibration frequency

- Maintaining drum level during mill power failure

- Cooling towers, weather inversions, ice related issues

- Port rodder maintenance, work done by contractors

- Smelt Dissolving tank draft, controlling

- Smelt Dissolving tank emergency steam agitation, frequency of testing, minimizing scaling of nozzles

- Leak detection systems, how are mills setting their alarm points

- Recovery boiler inspection for SAC, where have folks inspected, AF&PA document forthcoming

- Use of grade 24 materials in recovery boilers

- Rotork audit of iQ model rapid drain valves

- Secondary FD fan shut down as part of ESP, experience with combustibles

- Recovery boiler large leak trip logic implementation, example of activation

CLOSING COMMENTS:

CHAIRMAN: Gregory Burns

BLRBAC would like to recognize several members who have served BLRBAC over the years in leadership roles.  Its kind of like being elected to the BLRBAC hall of fame,

Those to be honored today are:

David Von Oepen

John Fredrickson

Everette Hume

John Kulig

Mike Blair

Bruce Knowlen – Plaque needs correction

David Avery – No Plaque

That concludes our Main Committee Meeting this morning.  Thank you all for your attendance and your time away from home and work.  Our next meeting will be October 6th, 7th And 8th 2025 and it will be here at the Hilton Hotel.  The Executive Committee strongly encourages you to register and stay at the Hilton.  Be on the lookout for that registration email in August.  Please spread the word to increase participation in these meetings.  We really need more participation from the mills.

With that I'll now entertain a motion to close the Main Committee meeting.   Second?    The Main committee Meeting is now closed.  We will have our Technical Presentation starting in about 15 minutes.

Thank you all and have a Safe trip back!

APPENDIX I

INCIDENT LIST

NO LEAK

No Leak

| Spring 2025A01 |  |
| --- | --- |
| Classification: | No Leak |
| Co, Mill, Location: | Clearwater Paper, Lewiston ID |
| Unit Data: | RB#4,1971, Babcock and Wilcox, PR-149, Drums - 2, DCE - NO, Floor - Sloped to rear |
| Unit Size: | 1.48 MMlb DS/day, 235,000 lb/hr steam, 600 PSIG, 740oF, 720 PSIG Design |
| Incident Date/Time: | December 31, 2023, Earliest Indication: 12/31/2023 at 7:05am |
| Downtime hrs, leak/total: | 5 days 5 hours |
| ESP? | YES |
| Leak/Incident Loc: | No Leak |
| How discovered: | Delta V Trend Feed Water to Steam Differential |
| Wash adjacent tube: | NO |
| Root cause: | No Leak, |
| Leak detection: | YES |
| Bed cooling enhance | NO |
| Last full inspection: | Nov-22 |
| Sequence of events: | On December 31, 2023 at 7:05am the FW/Steam differential spiked from 0 to 8.3. Operations starting performing a walk down to visually and audibly inspect for a leak. After a walkdown was performed the supervisor called the Asst. Superintendent to notify the issue. A conversation was had on if anyone had opened any manual blowdown valves and if PO4 was dropping? P04 had been stable with no significant drop. P04 was trending between 16.8-17 and operations had not performed any manual blowdowns. ID Fans showed no signs of significant increases. All other trends unchanged for flue gas concentration and precip function. 9:20 AM – TRASAR System alarm came into the system for PO4/concentrated boiler water leak After another walk down with no findings or indications of where a leak may be located on the boiler, the boiler was ESP’d at 9:56am. The boiler bed was then probed for temperatures over the next several days until the temperature was under 800 degrees. The boiler was water washed on 1/3/24 at 6:46pm. 1/4/24 AM – Hydro test started - Pressure was held at 600psig starting at 7:43am. Hydro was held for 2hrs 5mins at the 600psig pressure. No internal findings could be identified. External lagging was removed on the boiler to inspect for suspected leak at a buckstay 4 floors below sootblowers. No findings were present and water was determined to be residual from water washing. Hydro pressure increased at 9:48am to 650psig this was held until 11:12pm and no leak indications could be found. Ops group discussed any other areas that could have been missed on the walk down and decided to hold pressure at 600psig one more time to make sure no leaks were present from 1:01pm to 2:34pm. At this point a dry hydro was called. The boiler was then brought up on the curve and back online pushing steam at 1/5/24 at 12:25am. |
| Repair procedure: | No Leak Found |
| Future prevention: | SOP refined for detailed walkdown on suspicion of leak |

SMELT SPOUT/Dissolving Tank

Smelt Spout, No Leak

| Spring 2025A02 |  |
| --- | --- |
| Classification: | No Leak |
| Co, Mill, Location: | ND Paper, Rumford Mill, Rumford, Maine |
| Unit Data: | RB#PR-197,1981, B&W, BW-24523, Drums - 2, DCE - NO, Floor - Sloped to Front |
| Unit Size: | 4.4 MMlb DS/day, 640,000 lb/hr steam, 1300 PSIG, 849oF, 1450 PSIG Design |
| Incident Date/Time: | October 3, 2024, Earliest Indication: 10/3/2024 at 05:00pm |
| Downtime hrs, leak/total: | 30hrs |
| ESP? | NO |
| Leak/Incident Loc: | Smelt Spout, Wall box refractory washed out, no leak. |
| How discovered: | Other, On completion of the waterwash on a walkdown. |
| Wash adjacent tube: | NO |
| Root cause: | Fatigue, Refractory wash out on smelt spout wall box. |
| Leak detection: | NO |
| Bed cooling enhanc | NO |
| Last full inspection: | Sep-23 |
| Sequence of events: | The event occurred during a scheduled waterwash on the Rumford Mill’s C-Recovery Boiler on October 3rd, 2024.The Recovery unit was down at the time of the discovery for the waterwash with no pressure on the boiler and temperature at normal room temperature. Upon completion of the waterwash it was discovered on a walkdown of the boiler that the #4 smelt spout had water running out of the flange around the portion of the smelt spout that was bolted to the furnace side wall. Refractory wash-out was suspected to be the culprit. The #4 smelt spout was removed and we identified erosion on the refractory behind the smelt spout. |
| Repair procedure: | Pulled spout off, Hydroblasted and repoured refractory in wall box. Hydro-blasted refractory from Spout refractory wall box and furnace seal area in front of the smelt spout. Replaced missing furnace refractory and repoured wall box. The existing smelt spout was reused. |
| Future prevention: | Inspect smelt spout thoroughly during waterwashes |

Dissolving Tank Explosion

| Spring 2025A03 |  |
| --- | --- |
| Classification: | Dissolving Tank Explosion #45 |
| Co, Mill, Location: | International Paper, Mansfield Mill, Mansfield, Louisiana |
| Unit Data: | RB#1,1982, Babcock and Wilcox, 524-0199, Drums - 2, DCE - NO, Floor - Sloped to rear |
| Unit Size: | 4.052 MMlb DS/day, 488,000 lb/hr steam, 1275 PSIG, 900oF, 1475 PSIG Design |
| Incident Date/Time: | December 25, 2024, Earliest Indication: 12/25/2024 at 9:45 am |
| Downtime hrs, leak/total: | None |
| ESP? | NO |
| Leak/Incident Loc: | Dissolving Tank, #3 Spout upper mini hood damage |
| How discovered: | Other, After noise from dissolving tank violence stopped, operator inspected spout deck and found damage |
| Wash adjacent tube: | NO |
| Root cause: | Other, Build up on the rear wall (boiler has a sloped floor with spouts on rear wall) sloughed off in front of #3 spout, formed a dam and led to an excess smelt run off event. |
| Leak detection: | YES |
| Bed cooling enhanc | NO |
| Last full inspection: | February 2024 |
| Sequence of events: | The incident occurred 12/25/2024 approximately 9:45 am. Neither day nor night shift operator saw any signs of excessive smelt flow or noisy dissolving tank activity leading up to the event. Shatter jets were reported to be in good operating condition and doghouse showers had adequate flow prior to the event. The violence at the spout lasted approximately 15 minutes. We immediately reduced fuel to the boiler and when it became safe to access the area, we mechanically plugged the spout. Boiler operation was then returned to normal as the smelt flow per spout was within the OEM guidelines. Partial repair of the damage and restoring shatter jet capability was completed on a field day and the full repair has since been completed. Currently back at a four-spout operation. Cooling water flow to the plugged opening spout was left on. |
| Repair procedure: | Plugged the spout mechanically and plan to run until annual outage. Partial repair restoring shatter jet capability in case the plug failed was completed on a field day. |
| Future prevention: | Follow up with OEM to further investigate better shatter jet designs to handle smelt rushes and evaluate the impact of the scrubber fan on air flow disturbances to smelt stream that prevent proper shattering. Evaluate changes on liquor nozzles and holders to improve liquor distribution to the bed that minimize excessive wall shedding. |

ECONOMIZER

Economizer

| Spring 2025A04 |  |
| --- | --- |
| Classification: | Noncritical |
| Co, Mill, Location: | Clearwater Paper, Lewiston ID |
| Unit Data: | RB#4,1971, Babcock and Wilcox, PR-149, Drums - 2, DCE - NO, Floor - Sloped to rear |
| Unit Size: | 1.48 MMlb DS/day, 235,000 lb/hr steam, 600 PSIG, 740oF, 720 PSIG Design |
| Incident Date/Time: | March 13, 2024, Earliest Indication: 3/13/2024 at 2:45pm |
| Downtime hrs, leak/total: | 36 hours |
| ESP? | NO |
| Leak/Incident Loc: | Economizer Expansion Loop #11 from south, Economizer II |
| How discovered: | Operator Round |
| Wash adjacent tube: | NO |
| Root cause: | Stress Assisted Corrosion (SAC), |
| Leak detection: | YES |
| Bed cooling enhance | NO |
| Last full inspection: | Nov-22 |
| Sequence of events: | On 3/13/24 at approximately 2:45pm the Junior Field Operator was making rounds and found water running down the northwest corner of the south Economizer Hopper. They then called the Senior Field Operator to verify thereafter. With confirmation from both employees, they called the assistant superintendent to confirm as well. The control room was called and asked to pull the 1st spray at 3:01pm. The second spray was pulled at 3:21pm. After pulling the sprays and letting the boiler clear up the team was able to locate the leak. It was located in off the south wall 11 expansion tubes in on the hot side of the economizer. The boiler was then planned to conduct a controlled shut down burning out the bed and being able to bring a power boiler online to transfer mill steam demand onto to sustain mill run ability. The boiler was taken offline at 3:21am. The boiler was then cooled out in preparation for a boiler wash. The boiler wash was completed at 2pm on 3/14/24. Fireside and Waterside Lockouts were complete at 7pm. Initial inspection showed a pinhole leak on the expansion portion of the 11th pendant in from the south side. Contractors cut the tube above the existing butt weld and below on the compromised tube. A new expansion tube was installed. NDT inspection was completed using PT and RT on the weld out. RT was also done on the three tubes to the north and found no indications. Hydro started at 3/15/23 6:46am holding pressure above 600PSIG. Hydro passed at was completed at 7:25am. The boiler then started on the curve with gas in at 9:25am. Boiler online pushing steam at 2:06pm and liquor in the boiler at 3:52pm. |
| Repair procedure: | Sectioned tube and replaced with new economizer expansion loop. |
| Future prevention: | Performed RT on older style existing expansion loops in June outage, as a result replaced 3 other expansion loops based on RT. |

ECONOMIZER

| Spring 2025A05 |  |
| --- | --- |
| Classification: | Noncritical |
| Co, Mill, Location: | Mercer Celgar, Castlegar BC, Canada |
| Unit Data: | RB#2, 1993, Gotaverken, 61270 Drums - 1, DCE - NO, Floor - Sloped to Rear |
| Unit Size: | 3.3 MKG DS/day, 545 MT/hr steam, 6200 kPaG, 450oC, 10,800 kPaG Design |
| Incident Date/Time: | Earliest Indication: 6/12/2024 at 9:00 am |
| Downtime hrs, leak/total: | 72 hours off liquor to gas on |
| ESP? | NO |
| Leak/Incident Loc: | #2 Economizer |
| How discovered: | Water in ash hopper |
| Wash adjacent tube: | NO |
| Root cause: | Fatigue at seal weld on Economizer outlet tubing and casing |
| Leak detection: | NO |
| Bed cooling enhanc | NO |
| Last full inspection: | October 2023 |
| Sequence of events: | The field operator noticed water in the ash hopper and notified the Shift Engineer. The Steam Chief was called shortly after and notified of the leak, and started investigating if there was any indication of water entering the furnace. Further discussion was held with the SE and since there were no indications that there was water in the furnace, an orderly shutdown was started. As the boiler pressure reduced and the leak was identified to be on a weld between the furnace casing and economizer outlet. |
| Repair procedure: | The leak was repaired by excavation of the defect and WMBU. There was no tube sent out for lab analysis. |
| Future prevention: | Further inspection of adjacent joints and reinforcement of #2 Economizer in 2025 Outage |

Economizer

| Spring 2025A06 |  |
| --- | --- |
| Classification: | Critical #972 |
| Co, Mill, Location: | Canfor Pulp Limited, Northwood RB5, Prince George, BC |
| Unit Data: | RB#5, Started 1982, CE, CA-79120, Drums - 2, DCE - NO, Floor - Decanting |
| Unit Size: | 3.45 MMlb DS/day, 558,800 lb/hr steam, 652 PSIG, 752oF, 800 PSIG Design |
| Incident Date/Time: | August 15, 2024 Earliest Indication: 8/12/2024 |
| Downtime hrs, leak/total: | 60 hours (2 days 12hrs) |
| ESP? | NO |
| Leak/Incident Loc: | Economizer, upper economizer tube, very close to upper header connection. |
| How discovered: | Leak Detection System, Operator walkdowns pinpointed exact leak location |
| Wash adjacent tube: | NO |
| Root cause: | SAC |
| Leak detection: | YES |
| Bed cooling enhanced: | NO |
| Last full inspection: | Sep-23 |
| Sequence of events: | The leak detection balance trend showed there was likely a leak several days before the leak was visually identified (Figure 4 below). None of the boiler water residuals or chemical pump speeds were unusual so it was determined that the leak was likely in the economizer section. Several walk downs were completed with the sootblowers off over the next several days with no observable leaks or leak noises. #5 Recovery Boiler was operating at 3.2mmlb/day when the leak detection warning alarm activated in the control room at 1:30am on Aug 12th. The operating crew proceeded to shut down the sootblowers and do an acoustic walk down of the furnace. An audible steam leak was noted around the upper area of the furnace. |
| Repair procedure: | Weld overlay |
| Future prevention: |  |

Economizer

| Spring 2025A07 |  |
| --- | --- |
| Classification: | Noncritical |
| Co, Mill, Location: | Paper Excellence (Domtar), Skookumchuck, British Columbia Canada |
| Unit Data: | RB#1,1993 start up, ABB CA91105, Drums - 1, DCE - NO, Floor - Decanting |
| Unit Size: | 3.1 MMlb DS/day, 460,000 lb/hr steam, 630 PSIG, 750oF, 900 PSIG Design |
| Incident Date/Time: | October 22, 2024, Earliest Indication: 10/22/2024 at 14:15pm |
| Downtime hrs, leak/total: | 36 hrs |
| ESP? | NO |
| Leak/Incident Loc: | Economizer, rear economizer, 1st stage tube 64, Row2, lower horizontal header to tube connection |
| How discovered: | Walkdown, Economizer conveyor wet saltcake. |
| Wash adjacent tube: | NO |
| Root cause: | Weld Failure, root weld undercut |
| Leak detection: | NO |
| Bed cooling enhanc | NO |
| Last full inspection: | May-24 |
| Sequence of events: | October 22 at approximately 14:15pm Operator found wet saltcake in the Recovery boiler rear economizer hopper and reported it to the Shift Engineer immediately and water was verified in the hopper. Chief Engineer was contacted, and the decision was made to take the mill down in an orderly fashion. October 22 22:50hours the Recovery boiler was shutdown. October 23 11:00hours the leak was found in the lower righthand side, Tube 64, Row 2, 23:30hours weld repairs complete and final NDT passed. October 24 04:15am Hydro complete. October 24 10:50am Flame in Recovery boiler. |
| Repair procedure: | GTAW/SMAW with preheat |
| Future prevention: | Further NDT inspections |

Economizer

| Spring 2025A08 |  |
| --- | --- |
| Classification: | Noncritical |
| Co, Mill, Location: | Georgia Pacific, Brewton Al |
| Unit Data: | RB#No.4 ,2016, Andritz, A10166, Drums - 1, DCE - NO, Floor - Decanting |
| Unit Size: | 5.4 MMlb DS/day, 842,000 lb/hr steam, 1500 PSIG, 860oF, 1875 PSIG Design |
| Incident Date/Time: | 10-26-24 1:30 am Earliest Indication: 10/25/2024 at 1 am (Looking back through trends) |
| Downtime hrs, leak/total: | 24 |
| ESP? | NO |
| Leak/Incident Loc: | Economizer, Supply tube to header weld in #1 economizer, 2nd platen from left wall |
| How discovered: | Leak Detection System, |
| Wash adjacent tube: | NO |
| Root cause: | Weld Failure, Site of previous weld failure and repair. Original root cause was indetermined but thought to be a weld defect. (Fatigue from possible plugged header expansion seals was also considered). |
| Leak detection: | YES |
| Bed cooling enhanc | NO |
| Last full inspection: | Oct-23 |
| Sequence of events: | RBLI Mass alarm went off. Crews Called dept area leader to report that at the time water was not visible but crews found wet ash in econ 1 hopper. Team immediately reviewed trends found drop in Econ flue gas temp on same side (right). Plan developed for controlled shutdown 1.5 days out. RB4 was shut down for repair on 10/29 at 06:00. |
| Repair procedure: | Ground out and repaired weld |
| Future prevention: | Replacement of section of supply tube at header in April 2025 and inspection / clean-out of header expansion seals at casing. |

ECONOMIZER

| Spring 2025A09 |  |
| --- | --- |
| Classification: | Noncritical |
| Co, Mill, Location: | Mercer Celgar, Castlegar BC |
| Unit Data: | RB#2, 1992, Gotaverken, GO61270 Drums - 1, DCE - NO, Floor - Sloped to rear |
| Unit Size: | 3.3 MKG DS/day, 545 MT/hr steam, 6200 kPaG, 450oC, 10,800 kPaG Design |
| Incident Date/Time: | Earliest Indication: 12/12/2024 at 2:00 pm |
| Downtime hrs, leak/total: | Boiler was already down for non-related repairs |
| ESP? | NO |
| Leak/Incident Loc: | #2 Economizer upper section, |
| How discovered: | During pressure test completed to check for leaks |
| Wash adjacent tube: | NO |
| Root cause: | Stress Assisted Corrosion (SAC) (not confirmed by tube analysis). |
| Leak detection: | YES |
| Bed cooling enhanc | NO |
| Last full inspection: | October 2023 |
| Sequence of events: | There were no indications of a leak on any of our leak detection software, furnace pressure, noise, or id fan speeds. Boiler was down for non-related repairs. A pressure test was carried out to ensure boiler integrity. During the pressure test an internal leak was detected at the top of the #2 Economizer. |
| Repair procedure: |  |
| Future prevention: | Replacement of tube and further inspection by UT (phased array) |

Economizer

| Spring 2025A10 |  |
| --- | --- |
| Classification: | Noncritical |
| Co, Mill, Location: | International Paper, Mansfield Mill, Mansfield, Louisiana |
| Unit Data: | RB#1,1982, Babcock and Wilcox, 524-0199, Drums - 2, DCE - NO, Floor - Sloped to rear |
| Unit Size: | 3.2 MMlb DS/day, 488 lb/hr steam, 1275 PSIG, 900oF, 1475 PSIG Design |
| Incident Date/Time: | December 14, 2024, Earliest Indication: 12/12/2024 at 12:00 am |
| Downtime hrs, leak/total: | 69 hours liquor to liquor downtime |
| ESP? | NO |
| Leak/Incident Loc: | Economizer, one rupture tube leak in rear economizer row 4, tube #43 from the east and one tube plug leak in economizer row 3, tube #42 from the east. |
| How discovered: | Boiler Trip, |
| Wash adjacent tube: | YES |
| Root cause: | Weld Failure, A nearby previously plugged tube weld failed at the top plug weld causing water to spray on the adjacent tube that eventually thinned and failed with a fish mouth rupture. |
| Leak detection: | YES |
| Bed cooling enhanc | NO |
| Last full inspection: | February 18, 2024 |
| Sequence of events: | On Saturday December 14th at 3:53 PM, #1 Recovery Boiler tripped on High Furnace Draft. The outside recovery operator was out on the boiler assisting the recovery specialist with removing gas burners on the 2nd floor when he first noticed hot water pouring out of the floor drains. He started to investigate the source of hot water and found similar hot water flows at the 3rd and 4th floor drains. The operator continued to investigate until he found the source of the water to be the wet hopper (economizer). The wet hopper flush pump was down at the time and he suspected an economizer tube leak. He immediately went to the control room to tell the control room operator what he was seeing. At the time, the outside operator was unaware of the boiler trip. When the outside operator entered the control room, the control room operators were reviewing the boiler trip “first out” list. After communicating the observed water at the wet hopper, and based on the location of the water leak, the operators initiated an immediate shut down in lieu of an ESP. Data indicates that the weeping tube plug leak started about midnight on December the 12th. There was a rise of approximately 1KPPH in leak trends. This would not have been registered as a leak on the operator 4-hour review of leak trends. At the time of the tube rupture the leak trends did show a sudden significant deviation in mass flow. |
| Repair procedure: | The boiler contractor plugged the failed tube per guidance, repaired the leaking plug weld, and plugged three additional tubes due to thinning caused by washing as a result of the initial leak from the tube plug. |
| Future prevention: | The area of the leak is the site of three prior leaks, one of which was shortly after installation of the new economizer. Detailed inspection and investigation of manufacturing records did not clearly identify a root cause but suspect original manufacturing flaw and then repair flaws that leaked. The 2025 outage will include a more detailed inspection of the area, with refurbishment of some of the emergency plugs that were installed to ensure reliability. Inspection will look for porosity in welds at toe of the tube to header fillet weld. |

RISER. TUBE ABOVE ROOF TUBES

Riser, Tube Above Roof Tubes

| Spring 2025A11 |  |
| --- | --- |
| Classification: | Noncritical |
| Co, Mill, Location: | Billerud Quinnesec Mill, Quinnesec, MI |
| Unit Data: | RB##1,1985, B&W, PR203, Drums - 2, DCE - NO, Floor - Sloped to rear |
| Unit Size: | 4.68 MMlb DS/day, 634,000 lb/hr steam, 600 PSIG, 750oF, 800 PSIG Design |
| Incident Date/Time: | June 11, 2024, Earliest Indication: 6/11/2024 at 10:30 AM |
| Downtime hrs, leak/total: | 91.1 hrs |
| ESP? | NO |
| Leak/Incident Loc: | Riser, External to penthouse, crack at weld to penthouse |
| How discovered: | Walkdown, Operator noticed water on floor and investigated and found water dripping from boiler casing |
| Wash adjacent tube: | NO |
| Root cause: | Stress Assisted Corrosion (SAC) |
| Leak detection: | YES |
| Bed cooling enhanc | NO |
| Last full inspection: | May-24 |
| Sequence of events: | At about noon June 11, an operator reported water dripping to the floor from the boiler casing on the 9th floor. Department management went up to investigate. We removed some casing and insulation and at 13:03 were able to determine that the water was spraying from a riser tube, external to the penthouse, at the point where the riser tube penetrated through the penthouse casing. We made a call to our COE support to discuss what we had found and determine if an ESP was necessary. Were advised that an ESP seemed unnecessary but that we should execute an orderly but quick shutdown. We began reducing firing rate at 14:15 and were completely off liquor by 15:20. Smelt flow stopped at 15:50. All fuel was out of the boiler at 16:47. |
| Repair procedure: | Approximately 4 ft section of riser tube was removed and replaced |
| Future prevention: | To be determined – new tube was not welded to penthouse casing |

SUPERHEATER

Superheater

| Spring 2025A12 |  |
| --- | --- |
| Classification: | Noncritical |
| Co, Mill, Location: | Harmac Pacific, Nanaimo, British Columbia |
| Unit Data: | RB#5,1953, Combustion Engineering, CA-51126, Drums - 3, DCE - NO, Floor - Decanting |
| Unit Size: | 1.4 MMlb DS/day, 204,600 lb/hr steam, 600 PSIG, 750oF, 675 PSIG Design |
| Incident Date/Time: | September 4, 2024 00:29 |
| Downtime hrs, leak/total: | 59 HOURS |
| ESP? | YES |
| Leak/Incident Loc: | Superheater |
| How discovered: | Walkdown, Discovered during routine leak check |
| Wash adjacent tube: | NO |
| Root cause: | Fatigue, Two pin hole cracks were found at the top row of finger bar attachment welds on the low temperature superheater platens 16 and 19 at tube 23 |
| Leak detection: | NO |
| Bed cooling enhanc | NO |
| Last full inspection: | Apr-24 |
| Sequence of events: | 00:10 September 4, 2024 • Shift Engineer was informed by radio of a possible tube leak in #5 Recovery Boiler Generating Bank below the Steam Drum. The Recovery Assistant operator had just opened a furnace door as part of a routine leak check and thought he could hear a leak. • The Shift Engineer met the operator on the 6th floor at the door near the suspected leak • Opening the door, the Shift Engineer believed that he could see steam jetting from the Generating Bank tubes. 00:29 • ESP was initiated |
| Repair procedure: | The cracks were excavated, and weld metal build up repair was implemented |
| Future prevention: | Full replacement of the superheater is being planned. |

Superheater

| Spring 2025A13 |  |
| --- | --- |
| Classification: | Noncritical |
| Co, Mill, Location: | International Paper, Pensacola Mill, Cantonment FL |
| Unit Data: | RB#2,1975, Babcock & Wilcox, 21-0868, Drums - 2, DCE - NO, Floor - Sloped to rear |
| Unit Size: | 3.06 MMlb DS/day, 455,000 lb/hr steam, 850 PSIG, 850oF, 1000 PSIG Design |
| Incident Date/Time: | September 20, 2024, Earliest Indication: 9/20/2024 at 3:51 PM |
| Downtime hrs, leak/total: | 3hrs |
| ESP? | NO |
| Leak/Incident Loc: | Superheater, Superheater tube right under roof tube/penthouse shingle plates |
| How discovered: | Other, Boiler contractor and Reliability engineer noticed water leak while boiler was filling for hydro. |
| Wash adjacent tube: | NO |
| Root cause: | Other, Cutting torch caught a superheater tube while roof tubes were being cut out and replaced during annual outage. |
| Leak detection: | YES |
| Bed cooling enhanc | NO |
| Last full inspection: | Sep-24 |
| Sequence of events: | The leak was found on September 20, 2024 at approximately 3:51 PM. The boiler was being filled for a hydrostatic test following annual outage maintenance and capital pressure part work. The boiler was not online, and had no fire in the furnace, therefore no ESP was needed. Reliability engineer and contracted Boiler Maintenance (RMR) were making rounds while the boiler was filling and first noticed water entering the furnace, followed by water entering the penthouse from under a roof tube shingle plate as well. After the shingle plate was removed and the leak location was confirmed, operations stopped filling and started draining the boiler. The boiler maintenance contractor (RMR) then made the necessary repair. The leak was on the straight part of the upper superheater tube located roughly 1-2 feet under the roof tube shingle plate. The hole was roughly a 1–2-inch gash on the straight tube surrounded by good wall thickness |
| Repair procedure: | Weld Restoration |
| Future prevention: | Monitor and replace superheater tube section with Dutchman in future annual outage if it is warranted. Capital plan currently has a project to replace the superheater in the near future. |

Superheater

| Spring 2025A14 |  |
| --- | --- |
| Classification: | Noncritical |
| Co, Mill, Location: | Canfor Pulp Limited, Northwood RB5, Prince George, BC |
| Unit Data: | RB#5, Started 1982, CE, CA-79120, Drums - 2, DCE - NO, Floor - Decanting, |
| Unit Size: | 3.45 MMlb DS/day, 558,800 lb/hr steam, 652 PSIG, 752oF, 800 PSIG Design |
| Incident Date/Time: | October 29, 2024, Earliest Indication: 10/29/2024 |
| Downtime hrs, leak/total: | 144 hours (6 days) |
| ESP? | NO |
| Leak/Incident Loc: | Superheater, Found during hydrotest at stitch weld |
| How discovered: | Hydro Test, |
| Wash adjacent tube: | NO |
| Root cause: | Fatigue, Stitch weld cracking is common for this superheater |
| Leak detection: | NO |
| Bed cooling enhanced: | NO |
| Last full inspection: | Jul-22 |
| Sequence of events: | On October 29th, 2024 a hydrotest was being performed following an economizer section chemical clean. A leak was noted during the hydro inspections in the middle superheater platen 5, Tube 20 at one of the hinge pins (approx.7th floor elevation) (tie is actually a stitch weld). There were also 6 more hinge pin cracks on Platen 4 nearby that appeared close to opening up that the boiler makers repaired. This superheater has had several stitch weld cracks found during hydrotesting over the years so this is not uncommon for us. • Verified the leak, middle SH, platen 5, tube 20, left side, top row of stitch welds at the bottom toe of the weld. Platen #4 Top Row of Stitches (Set 8) Indications/non leaking cracks all on the bottom toes of the welds •Tube 16 (Stitch 16-17) •Tube 19 (Stitch 19-20) •Tube 20 (Stitch 20-21) •Tube 21 (Stitch 21-22) •Tube 23 (Stitch 23-24) •Tube24 (Stitch 24-25) |
| Repair procedure: | Removing stitch weld, repairing crack, and installing new hinge pin above or below |
| Future prevention: |  |

bOILER BANK SCREEN

Boiler Bank Screen

| Spring 2025A15 |  |
| --- | --- |
| Classification: | Critical #973 |
| Co, Mill, Location: | Domtar, Crofton, Crofton BC |
| Unit Data: | RB#3,1974, B&W, BW 70810, Drums - 2, DCE - NO, Floor - Sloped to rear |
| Unit Size: | 2.6 MMlb DS/day, 355,000 lb/hr steam, 600 PSIG, 725oF, 750 PSIG Design |
| Incident Date/Time: | October 24, 2024, Earliest Indication: 10/24/2024 at found on internal inspection |
| Downtime hrs, leak/total: | Leak was fixed during our outage. |
| ESP? | NO |
| Leak/Incident Loc: | Other, Rear wall hanger tube. |
| How discovered: | Other, during internal inspection of the boiler after it was shut down for annual outage. |
| Wash adjacent tube: | YES |
| Root cause: | Weld Failure, Old patch welded. SOFL |
| Leak detection: | YES |
| Bed cooling enhanc | NO |
| Last full inspection: | Mar-23 |
| Sequence of events: | Unfortunately, this leak was not noticed until the boiler was down and locked out for entry. Our NBIC inspector was crawling through the boiler and noticed the eroded metal around the tube and took the attached pictures. Given the amount of erosion, it is suspected the leak was there for some time. |
| Repair procedure: | Tube section was replaced |
| Future prevention: | Other tubes beside it were replaced. Washed tubes examined for wastage. Some WMBU on one tube. |

FURNACE SCREEN

Furnace Screen

| Spring 2025A16 |  |
| --- | --- |
| Classification: | Critical #974 |
| Co, Mill, Location: | Clearwater Paper, Lewiston ID |
| Unit Data: | RB#4,1971, Babcock and Wilcox, PR-149, Drums - 2, DCE - NO, Floor - Sloped to rear |
| Unit Size: | 1.48 MMlb DS/day, 235,000 lb/hr steam, 600 PSIG, 740oF, 720 PSIG Design |
| Incident Date/Time: | December 7, 2023, Earliest Indication: 12/7/2023 at 9:20 AM |
| Downtime hrs, leak/total: | 68 hours |
| ESP? | YES |
| Leak/Incident Loc: | Furnace Screen, Pendant #1 top tube of 4 vertically stacked |
| How discovered: | Leak Detection System, Nalco TRASAR System alarmed operator |
| Wash adjacent tube: | NO |
| Root cause: | Fatigue, Fatigue crack per metallurgist |
| Leak detection: | YES |
| Bed cooling enhance | NO |
| Last full inspection: | Nov-22 |
| Sequence of events: | On 12/7/23 at 9:20 Operator received alarm from TRASAR system for chemical balance. Operations began reviewing trends. It was seen that STM/FW differential increased around 7:10 AM that morning, with trend staying elevated but still below the normal alarm point for the system of 25 KPPH. ID fan was relatively unchanged with very slight increase. TRASAR blowdown concentration was shown to be decreasing starting at the same time. Operations started a walk down of the boiler with no findings. Hand valves were checked with mud drum blow downs being performed daily around the time of the suspected leak occurrence. 10:30 AM – liquor was pulled from the boiler. PO4 tests started to be taken every half hour showing slight decrease lining up with the online system, drawdowns performed on chemical feed pumps showed no change in feed rate. 12:17 PM – boiler was ESP’d for suspected concentrated boiler water leak with PO4 hand test falling from 16 at start of shift, to 14.1, 13.4, 12.1 approximately 30-45 minutes apart. 4:30 PM – Boiler was entered after 4 hour re-entry time 5:15 PM – All clear was given for entry into building, boiler was inspected with no visible internal signs of leakage. 12/8/23 3:30 PM - Bed measured to be cooled down below 800 Deg F 4:00 PM – Waterwash started 12/9/23 12:30 AM – Waterwash completed, boiler dry out started and filling for hydrotest started. 4:35 AM – Boiler up to pressure for hydro, walk down revealed leak on water cooled screen tube adjacent to left wall. 7:00 AM – Boiler drained; scaffold started to access repairs 10:00 AM – Scaffold in place, inspection confirmed leak at attachment weld where 5/8” square stock is used to hold screen section together vertically. 11:00 AM – Dutchman repairs started on 2” OD tube 5:30 PM – Dutchman repairs completed 8:00 PM – NDE completed with RT on welds, MT on other clips in the area on 4 similar accessible pendants with no other findings. Scaffold removal started. 12/10/23 1:30 AM – Hydro test passed post repairs. 3:30 AM – Boiler on the curve 8:00 AM – Boiler pushing steam to the header. 4:00 PM – First liquor spray in the boiler. |
| Repair procedure: | Sectioned tube and replaced with dutchman |
| Future prevention: | Performed MT on adjacent tubes accessible by scaffold in the furnace with no findings, plan to evaluate remaining attachments on upcoming full mill outage. During June 2024 outage no other findings were detected. |

uPPER FURNACE, ABOVE HIGHEST AIR ENTRY

Upper Furnace, above highest air entry

| Spring 2025A17 |  |
| --- | --- |
| Classification: | Noncritical |
| Co, Mill, Location: | International Paper, Pensacola Mill, Cantonment FL |
| Unit Data: | RB#2,1975, Babcock & Wilcox, 21-0868, Drums - 2, DCE - NO, Floor - Sloped to rear |
| Unit Size: | 3.06 MMlb DS/day, 455,000 lb/hr steam, 850 PSIG, 850oF, 1000 PSIG Design |
| Incident Date/Time: | September 20, 2024, Earliest Indication: 9/20/2024 at 12:36 PM |
| Downtime hrs, leak/total: | 1hr |
| ESP? | NO |
| Leak/Incident Loc: | Upper Furnace, above air entry, Water wall tube around buckstay area & soot blower panels |
| How discovered: | Walkdown, Boiler contractor & operations noticed small pin hole leak while boiler was filling up for hydro. |
| Wash adjacent tube: | NO |
| Root cause: | Fatigue, Metal flexing / weld heat zone from capital soot blower panel replacement next to tube leak area |
| Leak detection: | YES |
| Bed cooling enhanc | NO |
| Last full inspection: | Sep-24 |
| Sequence of events: | The leak was found on September 20, 2024 at approximately 12:36 PM. The boiler was being filled for a hydrostatic test following annual outage maintenance and capital pressure part work. The boiler was not online, and had no fire in the furnace, therefore no ESP was needed. Operator, Reliability engineer, and contracted Boiler Maintenance (RMR) were making rounds while the boiler was filling and noticed water was coming out from under a buckstay strap on the outside of the boiler water wall were the water wall tube meets the membrane wall. After the leak location was confirmed, operations stopped filling the boiler and the boiler maintenance contractor (RMR) made the necessary repair once the water level drained down below the leak location. The leak was on the cold side of a water wall tube where the tube is connected to the membrane metal on the right-hand side wall close to sootblower panels. The hole was about 1/16” diameter, surrounded by good wall thickness, including the adjacent tubes and membrane with no signs of further damage. |
| Repair procedure: | Weld Restoration |
| Future prevention: | Conduct further NDE inspection around buckstay area during next annual outage. |

Upper Furnace, above highest air entry

| Spring 2025A18 |  |
| --- | --- |
| Classification: | Critical #975 |
| Co, Mill, Location: | International Paper, Prattville, AL, USA |
| Unit Data: | RB#1,1967, CE, 1965, Drums - 2, DCE - Cascade, Floor - Decanting |
| Unit Size: | 2.47 MMlb DS/day, 320,000 lb/hr steam, 900 PSIG, 830oF, 1040 PSIG Design |
| Incident Date/Time: | October 17, 2024, Earliest Indication: 10/17/2024 at 4am |
| Downtime hrs, leak/total: | 0 |
| ESP? | NO |
| Leak/Incident Loc: | Upper Furnace, above air entry, RH Side Wall 8th Floor Mandoor Wall Box |
| How discovered: | Hydro Test, Low Pressure Hydro Test at Start of Acid Clean |
| Wash adjacent tube: | YES |
| Root cause: | Unknown, believed due to external stress at the closure plate weld in the bend. |
| Leak detection: | YES |
| Bed cooling enhanc | NO |
| Last full inspection: | Oct-23 |
| Sequence of events: | During hydrostatic test in preparation for the acid clean, under low pressure ~180 psi, employee supporting the acid clean hydro walk down noticed the water spray internally. After closer inspection, found a bent tube with a pin hole leak on the inside corner. Noted that the leak had also washed out the adjacent tube. |
| Repair procedure: | Pad weld prior to acid clean. Replaced tube with straight section post acid clean. |
| Future prevention: | Replace manway openings of this design. |

Upper Furnace, above highest air entry

| Spring 2025A19 |  |
| --- | --- |
| Classification: | Critical #976 |
| Co, Mill, Location: | Georgia Pacific, Brunswick Cellulose, Brunswick, GA |
| Unit Data: | RB#5,1972, Babcock and Wilcox, PR-145, Drums - 2, DCE - NO, Floor - Sloped to rear |
| Unit Size: | 4.1 MMlb DS/day, 551,000 lb/hr steam, 1250 PSIG, 816oF, 1450 PSIG Design |
| Incident Date/Time: | October 23, 2024, Earliest Indication: 10/23/2024 at 8:00AM |
| Downtime hrs, leak/total: | 171.5 |
| ESP? | NO |
| Leak/Incident Loc: | Upper Furnace, above air entry, two waterwall leaks on left side wall below manway opening above nose arch in SH section. (Manway is directly below a sootblower opening that had multiple leaks and subsequent ESP in July 2023). |
| How discovered: | Walkdown, Leak discovered by operator walkdown after the boiler had been taken down for maintenance of the primary air system |
| Wash adjacent tube: | YES |
| Root cause: | Thinning External, Manway opening was replaced during March 2024 annual outage after visual inspection and NDT indicated tubes below minimum wall. Panel was cut short during installation and leaks occurred in old wall tubes directly below panel. |
| Leak detection: | YES |
| Bed cooling enhanc | NO |
| Last full inspection: | Mar-24 |
| Sequence of events: | On 10/22/23 at approximately 5pm, boiler operators began shutting down recovery boiler to perform maintenance on primary air SCAH, damper and ductwork. After burning down bed, cooling, shutting down fans, and locking out fireside operators discovered leak during routine walkdown the following morning around 8am. The team decided not to ESP since the bed was already burned out and boiler was at 0 psi upon discovery. |
| Repair procedure: | Ultrasonically tested area around leak to identify extent of thinning and installed dutchmen below manway panel into nose arch. (Also UT’d nose arch tubes adjacent to side wall and found no thinning). |
| Future prevention: | Install full length 10-tube panel at manway opening fully extended into nose arch dead-air space during April 2025 outage. Continue NDT and visual inspections of all sootblower openings, upper furnace manways and wall tubes, and spot-check cold side corrosion. (Already implemented fire-to dry practices with continuous ignitors and SCAH in 2024). |

Upper Furnace, above highest air entry

| Spring 2025A20 |  |
| --- | --- |
| Classification: | Critical #977 |
| Co, Mill, Location: | Canfor Pulp Limited, Northwood RB5, Prince George, BC |
| Unit Data: | RB#5, Started 1982, CE, CA-79120, Drums - 2, DCE - NO, Floor - Decanting |
| Unit Size: | 3.45 MMlb DS/day, 558,800 lb/hr steam, 652 PSIG, 752oF, 800 PSIG Design |
| Incident Date/Time: | December 12, 2024 Earliest Indication: 12/12/2024 |
| Downtime hrs, leak/total: | S |
| ESP? | NO |
| Leak/Incident Loc: | Upper Furnace, above air entry, rear wall tube near the mud drum |
| How discovered: | Hydro Test |
| Wash adjacent tube: | NO |
| Root cause: | Thinning External, |
| Leak detection: | YES |
| Bed cooling enhanced: | NO |
| Last full inspection: | Sep-23 |
| Sequence of events: | RB5 was already down for an economizer tube leak repair. On the subsequent hydrotest, after repairing the economizer tube, this rear wall tube leak near the mud drum was discovered. |
| Repair procedure: | Weld metal buildup on failed tube to allow dry fire, but tube replacements will be required. RB5 is currently idle due to the mill reducing to a 1-line operation. |
| Future prevention: | Modify dry fire procedure and refractory seal |

iNTERNATIONAL INCIDENTS

UPPER FURNACE

| Spring 2025Ax1184 |  |
| --- | --- |
| Classification: | Intl |
| Co, Mill, Location: | Sylvamo, Mogi Guacu Mill |
| Unit Data: | RB#4,1957, B&W, PR-208, Drums - 2, DCE - Cyclone, Floor - Sloped to Front |
| Unit Size: | 0.652 MMlb DS/day, 76941.3 lb/hr steam, 400 PSIG, 680oF, 496 PSIG Design |
| Incident Date/Time: | September 1, 2024, Earliest Indication: 9/1/2024 at 06:00 pm |
| Downtime hrs, leak/total: | 13,40 hrs |
| ESP? | NO |
| Leak/Incident Loc: | Upper Furnace, above air entry, Right Wall near the beam opening |
| How discovered: | Other, During the beam management the maintenance team saw water coming out of the tube |
| Wash adjacent tube: | NO |
| Root cause: | Fatigue, External thinning, bad weld |
| Leak detection: | NO |
| Bed cooling enhanc | NO |
| Last full inspection: | Mar-24 |
| Sequence of events: | On the 1st of September during the beginning of a boiler wash with sootblowers the maintenance team were pulling the beams to allow the sootblowers to clean the boiler when they saw a small leaking coming out of the right wall tube. At the time of the detection the boiler was already cooled and with no pressure, the tube leaking was number 21 on the right wall. When the maintenance team saw the leak, they called the operational/inspection team to check the failure and decide how to repair it. |
| Repair procedure: | Weld tube with an overlay – Plan to replace the tube on 2025 annual outage |
| Future prevention: | Weld the membrane on the tube side – The tubes mapped with the same condition were already welded to prevent similar failure before next AO |

APPENDIX II

ESP  PRESENTATION

21 Total incidents reported and reviewed (20 US and Canada and 1 International)

There were zero Smelt Water Explosions, 1 ESP with no leak, 1 Smelt leak, 1 DT issue (Classified as an explosion), 11 were Non-critical and 6 incidents were Critical.

Three incidents were ESP’d. 1 with no leak, 1 with a SH leak and 1 Of the 6 critical incidents (6, 15, 16, 18, 19 and 20), one was found during an outage inspection, one was found on a walkdown when there was no bed in the boiler and two were found on a hydro.

Two were critical incidents which occurred in operation with a bed in the boiler.

One was a screen tube and one was an economizer tube behind the generating section with no baffle preventing water from reaching the furnace.

One of the two critical incidents in operation were ESP’d which amounted to 50% of the incidents that should have ESP’d, were actually ESP’d.

There were 7 economizer leaks, 3 super heater leaks, 1 screen tube leak, 5 upper furnace leaks, 1 external, 1 ESP with no leak, 1 smelt leak and 1 Dissolving tank incident (1 explosion with damage). Superheater and economizer leaks have typically been a larger portion of this chart and continue to be yet we have seen a larger percentage be upper furnace this session.

This slide is a side view of a recovery boiler showing approximate location and provides another view of the leak location. Some people like this type of view. It is not fully representative, as it does not also have a front view. Additionally, we now have added the section behind the nose for the generating section showing the location of a typical one drum boiler and two drum boiler leaks will also be shown in this location. The numbers in the circles are the incident numbers.

This chart is a total over the years from 2004 to present showing the total number of leaks per section and the average in each section. This is a 21.5-year total. We had 483 Economizer leaks (22.5 average), 155 Superheater leaks (7.2 average), 148 Upper furnace leaks (6.9 average), 113 Boiler bank leaks (5.3 average), 106 Lower furnace leaks (4.9 average), 43 Screen leaks (2.0 average) and 32 Smelt spout leaks (1.5 average). It is good to see that leaks in the more critical areas of the boiler are lower in frequency on the chart. The order has seemed to remain the same although SH and Upper furnace are getting closer.

These charts show the trend in number of leaks since 2004 for each section of the boiler (Economizer, Superheater, Boiler Bank, Screen, Upper furnace and lower furnace). We track these trends looking to see if we have made a difference in the number of leaks in each section based on improved OEM design, repair practices, procedures, etc. Previous charts did not take the number of boilers in service that year into account. I have now adjusted for the number of boilers in service that specific year and these trends do not show as drastic an improvement, but still an improvement. I think it is safe to say that although we are always focusing on eliminating leaks, we have not designed, maintained and operated any sections trouble free. Yet you will see later that we have now historically seen less explosions when critical leaks occur, so BLRBAC policies, systems and training have had a significant impact.

This slide shows incidents by boiler type. We have had 4 incidents reported in a one drum boiler, 15 incidents in a two drum boiler and 1 incident in a three drum boiler. We show 19 incidents in large economizer boilers and 1 in a cascade boiler. The larger number in large economizer boilers is likely due to a larger number of these type boilers being in service.

Regarding chart shows root cause of leaks, we had 2 thinning failures, 5 fatigue failures, 1 Thermal Fatigue, 4 SAC/SCC failures, 1 mechanical damage, and 4 weld failures. We continue to see SAC/SCC failures which is a mechanism to watch for with an aging fleet and large numbers of thermal cycles. Yet we are seeing failures due to Fatigue and Weld failures creep up.

This chart shows how the leaks were detected, and again it shows a high percentage found by the operators on walkdowns. These are typically in the 75% -90% range each session with this session being at just 50%. We had 10 found on walkdowns (One visually during an internal inspection on an outage).

We had 6 leaks reported found on a hydro this session and it begs the question if leak detection systems are sensitive enough. This also stresses the importance of training operators and the value of walkdowns.

We also had 4 leaks found through Leak detection systems.

We had 13 incidents reported with leak detection systems installed on the units (76% of the units). Three of the leak detection systems initially identified the leaks. It was identified that one leak detection system was trending upward when going back and looking at the data trends but it had not yet alarmed. As always, system detection sensitivity can play a part in the system’s ability to initially detect a leak or not.

This chart indicates the time from first discovery of a leak, to the time the unit was ESP’d. The time ranged from 19 minutes to 2 hours and 57 minutes. The average time was 2 hours and 20 minutes. As we know, evaluating a leak is a stressful and critical time. The time to act to ESP the unit on an actual leak is critical, and training and education can only help improve these times.

The two charts show Critical incidents to date. The first chart is the way we used to track it, just the straight number of critical incidents per year. I have now adjusted it to show a trend in Critical incidents per boiler. You can now see that it shows much larger rise in the number of critical leaks per boiler now that the number of boilers have been taken into account.

Looking at it solely for the last 20 years (Similar to the basis for the earlier charts), we do see an improved decreasing trend that we need to stay on.

The chart shows Boiler explosion history. So why if the number of critical incidents per boiler increased since 1966, did we see less explosions?

I would dare say that we have instituted better systems, equipment and guidelines to recognize, handle and prevent these incidents from having disastrous consequences.

We have instituted walkdowns as a prime example, which as you have seen, typically find 75 - 90% of leaks. Finding leaks early and reacting to them properly is just one example of the things we as an industry, working through BLRBAC, have done to proactively prevent bad situations from becoming worse.

This is a testament to everyone who has participated in the BLRBAC organization over the years and has been (And continues to be) a part of the constant learning, guideline development and operating diligence that it has taken to affect these results. It is also a testament to the operations people who do these walkdowns and discover leaks early and who have implemented the systems and procedures to handle them.

These charts show Dissolving tank explosions, Explosion history 5-year average and Explosions History per 100 operating years. We look at these charts to identify long term trends and improvements made. You see an uptick in the chart for explosions per 100 operating years. This last chart is a combined Recovery Boiler and Dissolving Tank chart. In the future, I will possibly look at separating them.

We know still that not all Dissolving tank incidents are being reported. We continue to encourage reporting dissolving tank near misses/plugged spouts/hood damage as incidents, so we can understand the issues leading to these incidents and be more preventative. We had 1 incident reported this session. We would like to encourage everyone to report these.

With this effort of reporting incidents, not just explosions, I feel we can have the same result as we have had with RB Explosion prevention through education, systems and guideline development.

This chart shows the number and age of units in North America. We have 116 units in the US and 25 in Canada for a total of 141. The average age in the US is 45 years and in Canada is 43 years. The maximum age in the US is 73 years and in Canada is 78 years. The oldest unit in operation is the Kruger Three rivers, PQ unit and it is a 1947 Ahlstrom Boiler. Please send Dean any updates.

These slides are the captured learnings from the incidents reported this session. I will go through each of these. The numbers at the end of each learning are the incident number from this session. i.e. Spring, 2025 session, incident number 01 (S25-01)

This slide discusses how to report incidents to BLRBAC and that we want incidents reported found on hydro. Even if found on hydro, we will classify these as critical if they are in a critical area even though the unit is not running. Sometimes they may have been leaking when the unit was on the way down. We are again also requesting that dissolving tank near misses also are reported so that we can learn from and address issues proactively. Please try to submit a separate incident when leaks occur in different sections of the boiler as they may be classified as Critical or Non-Critical differently.

This slide shows the information related to where to find the incident questionnaire and to look for confirmation from Dean Clay that it was received.

This slide shows where to find the Collection of incident learnings from Spring 2005 to Fall 2022 compiled by Dean Clay and soon to be updated by Mike Bruce and myself. The document describes how it is organized and the collective learnings over the years. I recommend this as a learning tool for management and operators for the prevention of future incidents.

The second item on the slide shows where to find the posted document of “How to get the most out of attending a BLRBAC meeting”. I highly encourage reading it and providing it to anyone in your mills planning on attending BLRBAC.

Downloadable presentation:

APPENDIX III

APPENDIX IV

Presentations

- Keit, Richard Salliss, IRmadillo - In-Situ Device for Green and Black Liquor Analysis

- Teknik Support, Johan Engvall, Smelt Spout Robot - Benefits of Automated Spout Rodding

- Valmet, Timo Karjunen, SimSmelt - Smelt Extraction and Floor Protection